## Controllers_Layout
| CNTRL 11/61 | [12 empty] | CNTRL 11/61
| AP1020 | [12 empty] | AP1020 EXT11-1 FRONT
| LOCATION | IO MODULE | USED CH | LOCATION | IO MODULE | USED CH | LOCATION | IO MODULE | USED CH | LOCATION |  | USED CH |  | LOCATION |  | USED CH | LOCATION |  | USED CH | LOCATION |  | USED CH | LOCATION |  | USED CH
| 11.1.1.1 | DI | 17 | 11.1.2.8 | DI | 20 | 11.1.3.1 | DI | 30 | 11.1.4.8 | DI | 27 |  | 11.1.5.1 | DI | 0 | 11.1.6.8 | AI | 0 | 11.1.7.1 |  | 0 | 11.1.8.8 |  | 0
| 11.1.1.2 | DI | 0 | 11.1.2.7 | DI | 22 | 11.1.3.2 | DI | 26 | 11.1.4.7 | DI | 2 |  | 11.1.5.2 | DI | 0 | 11.1.6.7 | SPARE | 0 | 11.1.7.2 |  | 0 | 11.1.8.7 |  | 0
| 11.1.1.3 | DI | 32 | 11.1.2.6 | DI | 23 | 11.1.3.3 | DI | 10 | 11.1.4.6 | DI | 0 |  | 11.1.5.3 | DI | 0 | 11.1.6.6 | SPARE | 0 | 11.1.7.3 |  | 0 | 11.1.8.6 |  | 0
| 11.1.1.4 | DO | 30 | 11.1.2.5 | DO | 30 | 11.1.3.4 | DO | 32 | 11.1.4.5 | DO | 15 |  | 11.1.5.4 | DO | 0 | 11.1.6.5 | SPARE | 0 | 11.1.7.4 |  | 0 | 11.1.8.5 |  | 0
| 11.1.1.5 | SPARE | 0 | 11.1.2.4 | SPARE | 0 | 11.1.3.5 | SPARE | 0 | 11.1.4.4 | AI | 14 |  | 11.1.5.5 | SPARE | 0 | 11.1.6.4 | SPARE | 0 | 11.1.7.5 |  | 0 | 11.1.8.4 |  | 0
| 11.1.1.6 | ELC | 0 | 11.1.2.3 | ELC | 0 | 11.1.3.6 | ELC | 0 | 11.1.4.3 | ELC | 0 |  | 11.1.5.6 | SPARE | 0 | 11.1.6.3 | SPARE | 0 | 11.1.7.6 |  | 0 | 11.1.8.3 |  | 0
| 11.1.1.7 | AI | 13 | 11.1.2.2 | AI | 15 | 11.1.3.7 | AI | 15 | 11.1.4.2 | AI | 16 |  | 11.1.5.7 | AI | 0 | 11.1.6.2 | SPARE | 0 | 11.1.7.7 |  | 0 | 11.1.8.2 |  | 0
| 11.1.1.8 | AO | 8 | 11.1.2.1 | AO | 6 | 11.1.3.8 | AO | 6 | 11.1.4.1 | AO | 0 |  | 11.1.5.8 | AO | 0 | 11.1.6.1 | SPARE | 0 | 11.1.7.8 |  | 0 | 11.1.8.1 |  | 0 | CNTRL
Terminal blocks required: |  | 304 |  |  | 304 |  |  | 304 |  |  | 304 |  |  |  | 304 |  |  | 32 | [7 empty] | AP
[10 empty] | 11.1.4.4 new AI added | [15 empty] | LOCATION | IO MODULE | USED CH | LOCATION | IO MODULE | USED CH | LOCATION | IO MODULE | USED CH | LOCATION | IO MODULE | USED CH
[26 empty] | 11.2.1.1 |  | 0 | 11.2.2.8 |  | 0 | 11.2.3.1 |  | 0 | 11.2.4.8 |  | 0
| CNTRL 12/62 | [12 empty] | CNTRL 12/62 | [11 empty] | 11.2.1.2 |  | 0 | 11.2.2.7 |  | 0 | 11.2.3.2 |  | 0 | 11.2.4.7 |  | 0
| AP1030 | [12 empty] | AP1030 | [11 empty] | 11.2.1.3 |  | 0 | 11.2.2.6 |  | 0 | 11.2.3.3 |  | 0 | 11.2.4.6 |  | 0
| LOCATION | IO MODULE | USED CH | LOCATION | IO MODULE | USED CH | LOCATION | IO MODULE | USED CH | LOCATION |  | USED CH |  | LOCATION |  | USED CH | LOCATION |  | USED CH | LOCATION |  | USED CH | LOCATION |  | USED CH | 11.2.1.4 |  | 0 | 11.2.2.5 |  | 0 | 11.2.3.4 |  | 0 | 11.2.4.5 |  | 0
| 12.1.1.1 | DI | 30 | 12.1.2.8 | DI | 27 | 12.1.3.1 | DI | 29 | 12.1.4.8 | DI | 26 |  | 12.1.5.1 | DI | 28 | 12.1.6.8 | DI | 25 | 12.1.7.1 | DI | 18 | 12.1.8.8 | DI | 27 | 11.2.1.5 |  | 0 | 11.2.2.4 |  | 0 | 11.2.3.5 |  | 0 | 11.2.4.4 |  | 0
| 12.1.1.2 | DI | 30 | 12.1.2.7 | DI | 30 | 12.1.3.2 | DI | 24 | 12.1.4.7 | DI | 3 |  | 12.1.5.2 | DI | 27 | 12.1.6.7 | DI | 27 | 12.1.7.2 | DI | 19 | 12.1.8.7 | DI | 28 | 11.2.1.6 |  | 0 | 11.2.2.3 |  | 0 | 11.2.3.6 |  | 0 | 11.2.4.3 |  | 0
| 12.1.1.3 | DI | 2 | 12.1.2.6 | DI | 6 | 12.1.3.3 | DI | 6 | 12.1.4.6 | DI | 6 |  | 12.1.5.3 | DI | 0 | 12.1.6.6 | DI | 24 | 12.1.7.3 | DI | 0 | 12.1.8.6 | DI | 17 | 11.2.1.7 |  | 0 | 11.2.2.2 |  | 0 | 11.2.3.7 |  | 0 | 11.2.4.2 |  | 0
| 12.1.1.4 | DO | 22 | 12.1.2.5 | DO | 39 | 12.1.3.4 | DO | 24 | 12.1.4.5 | DO | 31 |  | 12.1.5.4 | DO | 31 | 12.1.6.5 | DO | 30 | 12.1.7.4 | DO | 32 | 12.1.8.5 | DO | 2 | 11.2.1.8 |  | 0 | 11.2.2.1 |  | 0 | 11.2.3.8 |  | 0 | 11.2.4.1 |  | 0
| 12.1.1.5 | SPARE | 0 | 12.1.2.4 | SPARE | 0 | 12.1.3.5 | SPARE | 0 | 12.1.4.4 | SPARE | 0 |  | 12.1.5.5 | SPARE | 0 | 12.1.6.4 | SPARE | 0 | 12.1.7.5 | SPARE | 0 | 12.1.8.4 | SPARE | 0
| 12.1.1.6 | ELC | 0 | 12.1.2.3 | ELC | 0 | 12.1.3.6 | SPARE | 0 | 12.1.4.3 | SPARE | 0 |  | 12.1.5.6 | AI | 11 | 12.1.6.3 | AI | 15 | 12.1.7.6 | AI | 14 | 12.1.8.3 | AI | 16
| 12.1.1.7 | AI | 14 | 12.1.2.2 | AI | 2 | 12.1.3.7 | AI | 0 | 12.1.4.2 | AI | 0 |  | 12.1.5.7 | AI | 9 | 12.1.6.2 | AI | 8 | 12.1.7.7 | AI | 0 | 12.1.8.2 | AI | 0
| 12.1.1.8 | AO | 8 | 12.1.2.1 | SPARE | 0 | 12.1.3.8 | SPARE | 0 | 12.1.4.1 | SPARE | 0 |  | 12.1.5.8 | AO | 6 | 12.1.6.1 | AO | 7 | 12.1.7.8 | AO | 4 | 12.1.8.1 | SPARE | 0
Terminal blocks required: |  | 304 |  |  | 288 |  |  | 288 |  |  | 288 |  |  |  | 336 |  |  | 336 |  |  | 336 |  |  | 320
|  |  |  | 12.1.2.1 AO moved to 12.1.5.8 |  |  | 12.1.3.8 AO moved to 12.1.6.1 |  |  | 12.1.4.1 AO moved to 12.1.7.8
estimation
| Channel | CARD | CARD TYPE |  |  | Description |  |  | Cards Quantity | modules drop 11 | spare signals drop 11 | spare signals drop 11 % | modules drop 12 | spare signals drop 12 | spare signals drop 12 % | 11 | modules required | 12 | modules required |  | 31
5 | 32 | DI | 5X00605G01/1X00884H01 |  |  | 32-Channel Contact Input SOE |  |  | 39 | 15 | 271 | 56.46% | 24 | 309 | 40.23% | 209 | 6.5312 | 459 | 14.3438
5 | 32 | DO | 5X00500G01/1X00691H01 |  |  | 32-Channel 24 VDC DO |  |  | 13 | 5 | 53 | 33.12% | 8 | 45 | 17.58% | 107 | 3.3438 | 211 | 6.5938
3 | 16 | AI | 5X00784G01 |  |  | 16-Channel HART AI module |  |  | 19 | 7 | 39 | 34.82% | 12 | 103 | 53.65% | 73 | 4.5625 | 89 | 5.5625
1 | 8 | AO | 5X00062G01/5X00063G01 |  |  | 8-Ch HART AO |  |  | 9 | 5 | 20 | 50% | 4 | 7 | 21.88% | 20 | 2.5 | 25 | 3.125
|  | ELC | 5X00419G02/1X00569H01 | [5 empty] | 6 | 4 |  |  | 2
|  | SPARE | [6 empty] | 17 | 12 |  |  | 14
|  | SPARE OF modules% | [6 empty] | 16.5%

## IO LIST
Anc_100 | ID | old TAG | TAG | DESCRIPTION | LEN >55 | DUPL. TAG | SECTION | P&ID | FROM/TO | CABLE | MAS PANEL | TERMINAL BLOCK | TERMINALS | SIGNALS TYPICAL | SIGN. CODE | I/O TYPE | CHANNEL TYPE | LOGIC STATE / RANGE |  |  | UNITS | EXT. SUPPLY (V / A) | CU | RACK | SLOT | CHANNEL | total | HMI | NOTES | DELETED | REVISION |  |  |  |  | 1 | 2 | 3 | 4 | 5 |  | 6 |  |  |  | set description | reset description | range min | range max | units
8
ID-S01AP1030-00001 | 1 |  | A12PI0100 | press. PT0100 compr.air |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-003 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 10 | barG |  | 12 |  | 12.1.6.2 | 1 | 8 | AI |  |  | C | 12.1.6 | PT0100 compr.air |  | PT0100 | A12 | PI | 0100 |  |  |  |  | A12PI0100 | ok |  |  |  | 0 | 10 | barG
ID-S01AP1030-00002 | 2 |  | A17CK1106A_YLRE | compr. CK1106A lime pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 1 | 30 | DI |  |  | C | 12.1.1 | CK1106A lime pneu.convey. - in remote |  | CK1106A | A17 | CK | 1106 | A | _ | 11 | YLRE | A17CK1106A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00003 | 3 |  | A17CK1106A_YLH | compr. CK1106A lime pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 2 | 30 | DI |  |  | C | 12.1.1 | CK1106A lime pneu.convey. - in running |  | CK1106A | A17 | CK | 1106 | A | _ | 11 | YLH | A17CK1106A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00004 | 4 |  | A17CK1106A_YSG | compr. CK1106A lime pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 3 | 30 | DI |  |  | C | 12.1.1 | CK1106A lime pneu.convey. - supply fault |  | CK1106A | A17 | CK | 1106 | A | _ | 11 | YSG | A17CK1106A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00005 | 5 |  | A17CK1106A_HSH | compr. CK1106A lime pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 1 | 22 | DO |  |  | C | 12.1.1 | CK1106A lime pneu.convey. - start/stop |  | CK1106A | A17 | CK | 1106 | A | _ | 11 | HSH | A17CK1106A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00006 | 6 |  | A17CK1106B_YLRE | compr. CK1106B lime pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 1 | 27 | DI |  |  | C | 12.1.2 | CK1106B lime pneu.convey. - in remote |  | CK1106B | A17 | CK | 1106 | B | _ | 11 | YLRE | A17CK1106B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00007 | 7 |  | A17CK1106B_YLH | compr. CK1106B lime pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 2 | 27 | DI |  |  | C | 12.1.2 | CK1106B lime pneu.convey. - in running |  | CK1106B | A17 | CK | 1106 | B | _ | 11 | YLH | A17CK1106B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00008 | 8 |  | A17CK1106B_YSG | compr. CK1106B lime pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 3 | 27 | DI |  |  | C | 12.1.2 | CK1106B lime pneu.convey. - supply fault |  | CK1106B | A17 | CK | 1106 | B | _ | 11 | YSG | A17CK1106B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00009 | 9 |  | A17CK1106B_HSH | compr. CK1106B lime pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 1 | 39 | DO |  |  | C | 12.1.2 | CK1106B lime pneu.convey. - start/stop |  | CK1106B | A17 | CK | 1106 | B | _ | 11 | HSH | A17CK1106B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00010 | 10 |  | A17EH1120_YLH | elec.heater EH1120 lime silos SL1100 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.1.3 | 1 | 2 | DI |  |  | C | 12.1.1 | EH1120 lime silos SL1100 - in running |  | EH1120 | A17 | EH | 1120 |  | _ | 10 | YLH | A17EH1120_YLH | ok | [5 empty] | 0
ID-S01AP1030-00011 | 11 |  | A17EH1120_YSG | elec.heater EH1120 lime silos SL1100 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.1.3 | 2 | 2 | DI |  |  | C | 12.1.1 | EH1120 lime silos SL1100 - supply fault |  | EH1120 | A17 | EH | 1120 |  | _ | 10 | YSG | A17EH1120_YSG | ok | [5 empty] | 0
ID-S01AP1030-00012 | 12 |  | A17EH1120_HSH | elec.heater EH1120 lime silos SL1100 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 2 | 22 | DO |  |  | C | 12.1.1 | EH1120 lime silos SL1100 - start/stop |  | EH1120 | A17 | EH | 1120 |  | _ | 10 | HSH | A17EH1120_HSH | ok | [5 empty] | 0
ID-S01AP1030-00013 | 13 |  | A17EH1121A_YLH | elec.heater EH1121A lime conveyor SW1103A - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 4 | 30 | DI |  |  | C | 12.1.1 | EH1121A lime conveyor SW1103A - in running |  | EH1121A | A17 | EH | 1121 | A | _ | 11 | YLH | A17EH1121A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00014 | 14 |  | A17EH1121A_YSG | elec.heater EH1121A lime conveyor SW1103A - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 5 | 30 | DI |  |  | C | 12.1.1 | EH1121A lime conveyor SW1103A - supply fault |  | EH1121A | A17 | EH | 1121 | A | _ | 11 | YSG | A17EH1121A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00015 | 15 |  | A17EH1121A_HSH | elec.heater EH1121A lime conveyor SW1103A - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 3 | 22 | DO |  |  | C | 12.1.1 | EH1121A lime conveyor SW1103A - start/stop |  | EH1121A | A17 | EH | 1121 | A | _ | 11 | HSH | A17EH1121A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00016 | 16 |  | A17EH1121B_YLH | elec.heater EH1121B lime conveyor SW1103B - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 4 | 27 | DI |  |  | C | 12.1.2 | EH1121B lime conveyor SW1103B - in running |  | EH1121B | A17 | EH | 1121 | B | _ | 11 | YLH | A17EH1121B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00017 | 17 |  | A17EH1121B_YSG | elec.heater EH1121B lime conveyor SW1103B - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 5 | 27 | DI |  |  | C | 12.1.2 | EH1121B lime conveyor SW1103B - supply fault |  | EH1121B | A17 | EH | 1121 | B | _ | 11 | YSG | A17EH1121B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00018 | 18 |  | A17EH1121B_HSH | elec.heater EH1121B lime conveyor SW1103B - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 2 | 39 | DO |  |  | C | 12.1.2 | EH1121B lime conveyor SW1103B - start/stop |  | EH1121B | A17 | EH | 1121 | B | _ | 11 | HSH | A17EH1121B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00019 | 19 |  | A17EH1122A_YLH | elec.heater EH1122A lime conveyor SW1104A - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 6 | 30 | DI |  |  | C | 12.1.1 | EH1122A lime conveyor SW1104A - in running |  | EH1122A | A17 | EH | 1122 | A | _ | 11 | YLH | A17EH1122A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00020 | 20 |  | A17EH1122A_YSG | elec.heater EH1122A lime conveyor SW1104A - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 7 | 30 | DI |  |  | C | 12.1.1 | EH1122A lime conveyor SW1104A - supply fault |  | EH1122A | A17 | EH | 1122 | A | _ | 11 | YSG | A17EH1122A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00021 | 21 |  | A17EH1122A_HSH | elec.heater EH1122A lime conveyor SW1104A - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 4 | 22 | DO |  |  | C | 12.1.1 | EH1122A lime conveyor SW1104A - start/stop |  | EH1122A | A17 | EH | 1122 | A | _ | 11 | HSH | A17EH1122A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00022 | 22 |  | A17EH1122B_YLH | elec.heater EH1122B lime conveyor SW1104B - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 6 | 27 | DI |  |  | C | 12.1.2 | EH1122B lime conveyor SW1104B - in running |  | EH1122B | A17 | EH | 1122 | B | _ | 11 | YLH | A17EH1122B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00023 | 23 |  | A17EH1122B_YSG | elec.heater EH1122B lime conveyor SW1104B - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 7 | 27 | DI |  |  | C | 12.1.2 | EH1122B lime conveyor SW1104B - supply fault |  | EH1122B | A17 | EH | 1122 | B | _ | 11 | YSG | A17EH1122B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00024 | 24 |  | A17EH1122B_HSH | elec.heater EH1122B lime conveyor SW1104B - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 3 | 39 | DO |  |  | C | 12.1.2 | EH1122B lime conveyor SW1104B - start/stop |  | EH1122B | A17 | EH | 1122 | B | _ | 11 | HSH | A17EH1122B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00025 | 25 |  | A17EH1107A_YLH | elec.heater EH1107A lime 1th stage - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 8 | 30 | DI |  |  | C | 12.1.1 | EH1107A lime 1th stage - in running |  | EH1107A | A17 | EH | 1107 | A | _ | 11 | YLH | A17EH1107A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00026 | 26 |  | A17EH1107A_YSG | elec.heater EH1107A lime 1th stage - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 9 | 30 | DI |  |  | C | 12.1.1 | EH1107A lime 1th stage - supply fault |  | EH1107A | A17 | EH | 1107 | A | _ | 11 | YSG | A17EH1107A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00027 | 27 |  | A17EH1107A_HSH | elec.heater EH1107A lime 1th stage - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 5 | 22 | DO |  |  | C | 12.1.1 | EH1107A lime 1th stage - start/stop |  | EH1107A | A17 | EH | 1107 | A | _ | 11 | HSH | A17EH1107A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00028 | 28 |  | A17EH1107B_YLH | elec.heater EH1107B lime 1th stage - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 8 | 27 | DI |  |  | C | 12.1.2 | EH1107B lime 1th stage - in running |  | EH1107B | A17 | EH | 1107 | B | _ | 11 | YLH | A17EH1107B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00029 | 29 |  | A17EH1107B_YSG | elec.heater EH1107B lime 1th stage - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 9 | 27 | DI |  |  | C | 12.1.2 | EH1107B lime 1th stage - supply fault |  | EH1107B | A17 | EH | 1107 | B | _ | 11 | YSG | A17EH1107B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00030 | 30 |  | A17EH1107B_HSH | elec.heater EH1107B lime 1th stage - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 4 | 39 | DO |  |  | C | 12.1.2 | EH1107B lime 1th stage - start/stop |  | EH1107B | A17 | EH | 1107 | B | _ | 11 | HSH | A17EH1107B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00031 | 31 |  | A17EH1108A_YLH | elec.heater EH1108A lime 2th stage - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 10 | 30 | DI |  |  | C | 12.1.1 | EH1108A lime 2th stage - in running |  | EH1108A | A17 | EH | 1108 | A | _ | 11 | YLH | A17EH1108A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00032 | 32 |  | A17EH1108A_YSG | elec.heater EH1108A lime 2th stage - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 11 | 30 | DI |  |  | C | 12.1.1 | EH1108A lime 2th stage - supply fault |  | EH1108A | A17 | EH | 1108 | A | _ | 11 | YSG | A17EH1108A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00033 | 33 |  | A17EH1108A_HSH | elec.heater EH1108A lime 2th stage - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 6 | 22 | DO |  |  | C | 12.1.1 | EH1108A lime 2th stage - start/stop |  | EH1108A | A17 | EH | 1108 | A | _ | 11 | HSH | A17EH1108A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00034 | 34 |  | A17EH1108B_YLH | elec.heater EH1108B lime 2th stage - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 10 | 27 | DI |  |  | C | 12.1.2 | EH1108B lime 2th stage - in running |  | EH1108B | A17 | EH | 1108 | B | _ | 11 | YLH | A17EH1108B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00035 | 35 |  | A17EH1108B_YSG | elec.heater EH1108B lime 2th stage - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 11 | 27 | DI |  |  | C | 12.1.2 | EH1108B lime 2th stage - supply fault |  | EH1108B | A17 | EH | 1108 | B | _ | 11 | YSG | A17EH1108B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00036 | 36 |  | A17EH1108B_HSH | elec.heater EH1108B lime 2th stage - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 5 | 39 | DO |  |  | C | 12.1.2 | EH1108B lime 2th stage - start/stop |  | EH1108B | A17 | EH | 1108 | B | _ | 11 | HSH | A17EH1108B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00037 | 37 |  | A17EH1109A_YLH | elec.heater EH1109A lime 3th stage - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 12 | 30 | DI |  |  | C | 12.1.1 | EH1109A lime 3th stage - in running |  | EH1109A | A17 | EH | 1109 | A | _ | 11 | YLH | A17EH1109A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00038 | 38 |  | A17EH1109A_YSG | elec.heater EH1109A lime 3th stage - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 13 | 30 | DI |  |  | C | 12.1.1 | EH1109A lime 3th stage - supply fault |  | EH1109A | A17 | EH | 1109 | A | _ | 11 | YSG | A17EH1109A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00039 | 39 |  | A17EH1109A_HSH | elec.heater EH1109A lime 3th stage - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 7 | 22 | DO |  |  | C | 12.1.1 | EH1109A lime 3th stage - start/stop |  | EH1109A | A17 | EH | 1109 | A | _ | 11 | HSH | A17EH1109A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00040 | 40 |  | A17EH1109B_YLH | elec.heater EH1109B lime 3th stage - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 12 | 27 | DI |  |  | C | 12.1.2 | EH1109B lime 3th stage - in running |  | EH1109B | A17 | EH | 1109 | B | _ | 11 | YLH | A17EH1109B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00041 | 41 |  | A17EH1109B_YSG | elec.heater EH1109B lime 3th stage - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 13 | 27 | DI |  |  | C | 12.1.2 | EH1109B lime 3th stage - supply fault |  | EH1109B | A17 | EH | 1109 | B | _ | 11 | YSG | A17EH1109B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00042 | 42 |  | A17EH1109B_HSH | elec.heater EH1109B lime 3th stage - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 6 | 39 | DO |  |  | C | 12.1.2 | EH1109B lime 3th stage - start/stop |  | EH1109B | A17 | EH | 1109 | B | _ | 11 | HSH | A17EH1109B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00043 | 43 |  | A17FN1105A_YLH | fan FN1105A cooling lime M1104A - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 14 | 30 | DI |  |  | C | 12.1.1 | FN1105A cooling lime M1104A - in running |  | FN1105A | A17 | FN | 1105 | A | _ | 11 | YLH | A17FN1105A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00044 | 44 |  | A17FN1105A_YSG | fan FN1105A cooling lime M1104A - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 15 | 30 | DI |  |  | C | 12.1.1 | FN1105A cooling lime M1104A - supply fault |  | FN1105A | A17 | FN | 1105 | A | _ | 11 | YSG | A17FN1105A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00045 | 45 |  | A17FN1105A_HSH | fan FN1105A cooling lime M1104A - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 8 | 22 | DO |  |  | C | 12.1.1 | FN1105A cooling lime M1104A - start/stop |  | FN1105A | A17 | FN | 1105 | A | _ | 11 | HSH | A17FN1105A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00046 | 46 |  | A17FN1105B_YLH | fan FN1105B cooling lime M1104B - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 14 | 27 | DI |  |  | C | 12.1.2 | FN1105B cooling lime M1104B - in running |  | FN1105B | A17 | FN | 1105 | B | _ | 11 | YLH | A17FN1105B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00047 | 47 |  | A17FN1105B_YSG | fan FN1105B cooling lime M1104B - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 15 | 27 | DI |  |  | C | 12.1.2 | FN1105B cooling lime M1104B - supply fault |  | FN1105B | A17 | FN | 1105 | B | _ | 11 | YSG | A17FN1105B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00048 | 48 |  | A17FN1105B_HSH | fan FN1105B cooling lime M1104B - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 7 | 39 | DO |  |  | C | 12.1.2 | FN1105B cooling lime M1104B - start/stop |  | FN1105B | A17 | FN | 1105 | B | _ | 11 | HSH | A17FN1105B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00049 | 49 |  | A17FSL1106A | flow L FSL1106A lime pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 1 | 27 | DI |  |  | C | 12.1.5 | L FSL1106A lime pneu.convey. | L |  | A17 | FSL | 1106 | A |  |  |  | A17FSL1106A | ok | [5 empty] | 0
ID-S01AP1030-00050 | 50 |  | A17FSL1106B | flow L FSL1106B lime pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 1 | 24 | DI |  |  | C | 12.1.6 | L FSL1106B lime pneu.convey. | L | L | A17 | FSL | 1106 | B |  |  |  | A17FSL1106B | ok | [5 empty] | 0
ID-S01AP1030-00051 | 51 |  | A17HV1101A_ZSH | vlv. HV1101A extract. lime silos SL1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 2 | 27 | DI |  |  | C | 12.1.5 | HV1101A extract. lime silos SL1100 - opened |  | HV1101A | A17 | HV | 1101 | A | _ | 11 | ZSH | A17HV1101A_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00052 | 52 |  | A17HV1101B_ZSH | vlv. HV1101B extract. lime silos SL1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.6 | 2 | 24 | DI |  |  | C | 12.1.6 | HV1101B extract. lime silos SL1100 - opened |  | HV1101B | A17 | HV | 1101 | B | _ | 11 | ZSH | A17HV1101B_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00053 | 53 |  | A17LP1100_YL | loc.pan. LP1100 filling lime SL1100 - reset |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | attivo | 0 |  | 12 |  | 12.1.4.8 | 1 | 26 | DI |  |  | C | 12.1.4 | LP1100 filling lime SL1100 - reset |  | LP1100 | A17 | LP | 1100 |  | _ | 10 | YL | A17LP1100_YL | ok | [5 empty] | 0
ID-S01AP1030-00054 | 54 |  | A17LP11100_YSA | loc.pan. LP1100 filling lime SL1100 - charge alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 1 | 31 | DO |  |  | C | 12.1.4 | LP1100 filling lime SL1100 - charge alarm |  | LP1100 | A17 | LP | 11100 |  | _ | 11 | YSA | A17LP11100_YSA | ok | [5 empty] | 0
ID-S01AP1030-00055 | 55 |  | A17LP11100_YLRE | loc.pan. LP1100 filling lime SL1100 - charge ready |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 2 | 31 | DO |  |  | C | 12.1.4 | LP1100 filling lime SL1100 - charge ready |  | LP1100 | A17 | LP | 11100 |  | _ | 11 | YLRE | A17LP11100_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00056 | 56 |  | A17LP11100_LAHH | loc.pan. LP1100 filling lime SL1100 - visive alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 3 | 31 | DO |  |  | C | 12.1.4 | LP1100 filling lime SL1100 - visive alarm |  | LP1100 | A17 | LP | 11100 |  | _ | 11 | LAHH | A17LP11100_LAHH | ok | [5 empty] | 0
ID-S01AP1030-00057 | 57 |  | A17LP21100_LAHH | loc.pan. LP1100 filling lime SL1100 - acustic alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 4 | 31 | DO |  |  | C | 12.1.4 | LP1100 filling lime SL1100 - acustic alarm |  | LP1100 | A17 | LP | 21100 |  | _ | 11 | LAHH | A17LP21100_LAHH | ok | [5 empty] | 0
ID-S01AP1030-00058 | 58 |  | A17LP11100_LI | loc.pan. LP1100 filling lime SL1100 - Level indicator |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LP1100 filling lime SL1100 - Level indicator |  | LP1100 | A17 | LP | 11100 |  | _ | 11 | LI | A17LP11100_LI | ok | [5 empty] | %
ID-S01AP1030-00059 | 59 |  | A17CD1300_YLRE | aut.pan. AP1300 cleaning lime FF1100 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.4.8 | 2 | 26 | DI |  |  | C | 12.1.4 | AP1300 cleaning lime FF1100 - in remote |  | AP1300 | A17 | CD | 1300 |  | _ | 10 | YLRE | A17CD1300_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00060 | 60 |  | A17CD1300_YSA | aut.pan. AP1300 cleaning lime FF1100 - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.4.8 | 3 | 26 | DI |  |  | C | 12.1.4 | AP1300 cleaning lime FF1100 - com.alarm |  | AP1300 | A17 | CD | 1300 |  | _ | 10 | YSA | A17CD1300_YSA | ok | [5 empty] | 0
ID-S01AP1030-00061 | 61 |  | A17CD1300_HSH | aut.pan. AP1300 cleaning lime FF1100 - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 12 |  | 12.1.4.5 | 5 | 31 | DO |  |  | C | 12.1.4 | AP1300 cleaning lime FF1100 - enable |  | AP1300 | A17 | CD | 1300 |  | _ | 10 | HSH | A17CD1300_HSH | ok | [5 empty] | 0
ID-S01AP1030-00062 | 62 |  | A17LSH1101A | lev. H LSH1101A lime hopper HP1101A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 3 | 27 | DI |  |  | D | 12.1.5 | H LSH1101A lime hopper HP1101A |  | H | A17 | LSH | 1101 | A |  |  |  | A17LSH1101A | ok | [5 empty] | 0
ID-S01AP1030-00063 | 63 |  | A17LSH1101B | lev. H LSH1101B lime hopper HP1101B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 3 | 24 | DI |  |  | D | 12.1.6 | H LSH1101B lime hopper HP1101B |  | H | A17 | LSH | 1101 | B |  |  |  | A17LSH1101B | ok | [5 empty] | 0
ID-S01AP1030-00064 | 64 |  | A17LSHH1100 | lev. HH LSHH1100 lime silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.6.7 | 1 | 27 | DI |  |  | D | 12.1.6 | HH LSHH1100 lime silos SL1100 |  | HH | A17 | LSHH | 1100 |  |  |  |  | A17LSHH1100 | ok | [5 empty] | 0
ID-S01AP1030-00065 | 65 |  | A17LSL1101A | lev. L LSL1101A lime hopper HP1101A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 4 | 27 | DI |  |  | D | 12.1.5 | L LSL1101A lime hopper HP1101A |  | L | A17 | LSL | 1101 | A |  |  |  | A17LSL1101A | ok | [5 empty] | 0
ID-S01AP1030-00066 | 66 |  | A17LSL1101B | lev. L LSL1101B lime hopper HP1101B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 4 | 24 | DI |  |  | D | 12.1.6 | L LSL1101B lime hopper HP1101B |  | L | A17 | LSL | 1101 | B |  |  |  | A17LSL1101B | ok | [5 empty] | 0
ID-S01AP1030-00067 | 67 |  | A17LSLL1100 | lev. LL LSLL1100 lime silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.6.7 | 2 | 27 | DI |  |  | D | 12.1.6 | LL LSLL1100 lime silos SL1100 |  | LL | A17 | LSLL | 1100 |  |  |  |  | A17LSLL1100 | ok | [5 empty] | 0
ID-S01AP1030-00068 | 68 |  | A17LI1100 | lev. LT1100 lime silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LT1100 lime silos SL1100 |  | LT1100 | A17 | LI | 1100 |  |  |  |  | A17LI1100 | ok | [5 empty] | %
ID-S01AP1030-00069 | 69 |  | A17POV1102A_ZSH | vlv. POV1102A extract. lime silos SL1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 5 | 27 | DI |  |  | C | 12.1.5 | POV1102A extract. lime silos SL1100 - opened |  | POV1102A | A17 | POV | 1102 | A | _ | 12 | ZSH | A17POV1102A_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00070 | 70 |  | A17POV1102A_HSH | vlv. POV1102A extract. lime silos SL1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | A17LP1102 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.1.4 | 9 | 22 | DO |  |  | C | 12.1.1 | POV1102A extract. lime silos SL1100 - open |  | POV1102A | A17 | POV | 1102 | A | _ | 12 | HSH | A17POV1102A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00071 | 71 |  | A17POV1102A_HSL | vlv. POV1102A extract. lime silos SL1100 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | A17LP1102 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.1.4 | 10 | 22 | DO |  |  | C | 12.1.1 | POV1102A extract. lime silos SL1100 - close |  | POV1102A | A17 | POV | 1102 | A | _ | 12 | HSL | A17POV1102A_HSL | ok | [5 empty] | 0
ID-S01AP1030-00072 | 72 |  | A17POV1102B_ZSH | vlv. POV1102B extract. lime silos SL1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.6 | 5 | 24 | DI |  |  | C | 12.1.6 | POV1102B extract. lime silos SL1100 - opened |  | POV1102B | A17 | POV | 1102 | B | _ | 12 | ZSH | A17POV1102B_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00073 | 73 |  | A17POV1102B_HSH | vlv. POV1102B extract. lime silos SL1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | A17LP1102 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.2.5 | 8 | 39 | DO |  |  | C | 12.1.2 | POV1102B extract. lime silos SL1100 - open |  | POV1102B | A17 | POV | 1102 | B | _ | 12 | HSH | A17POV1102B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00074 | 74 |  | A17POV1102B_HSL | vlv. POV1102B extract. lime silos SL1100 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | A17LP1102 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.2.5 | 9 | 39 | DO |  |  | C | 12.1.2 | POV1102B extract. lime silos SL1100 - close |  | POV1102B | A17 | POV | 1102 | B | _ | 12 | HSL | A17POV1102B_HSL | ok | [5 empty] | 0
ID-S01AP1030-00075 | 75 |  | A17PSHH1100 | pres. HH PSHH1100 lime compr.air FF1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.7 | 3 | 27 | DI |  |  | C | 12.1.6 | HH PSHH1100 lime compr.air FF1100 |  | HH | A17 | PSHH | 1100 |  |  |  |  | A17PSHH1100 | ok | [5 empty] | 0
ID-S01AP1030-00076 | 76 |  | A17PSL1301 | pres. L PSL1301 lime compr.air PRV1301 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.7 | 4 | 27 | DI |  |  | C | 12.1.6 | L PSL1301 lime compr.air PRV1301 |  | L | A17 | PSL | 1301 |  |  |  |  | A17PSL1301 | ok | [5 empty] | 0
ID-S01AP1030-00077 | 77 |  | A17PI1106A | press. PT1106A lime pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 4000 | mmH20 |  | 12 |  | 12.1.5.7 | 1 | 9 | AI |  |  | C | 12.1.5 | PT1106A lime pneu.convey. |  | PT1106A | A17 | PI | 1106 | A |  |  |  | A17PI1106A | ok |  |  |  | 0 | 4000 | mmH20
ID-S01AP1030-00078 | 78 |  | A17PI1106B | press. PT1106B lime pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 4000 | mmH20 |  | 12 |  | 12.1.5.7 | 2 | 9 | AI |  |  | C | 12.1.5 | PT1106B lime pneu.convey. |  | PT1106B | A17 | PI | 1106 | B |  |  |  | A17PI1106B | ok |  |  |  | 0 | 4000 | mmH20
ID-S01AP1030-00079 | 79 |  | A17RV1110A_YLRE | rot.vlv. RV1110A lime pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 1 | 30 | DI |  |  | C | 12.1.1 | RV1110A lime pneu.convey. - in remote |  | RV1110A | A17 | RV | 1110 | A | _ | 11 | YLRE | A17RV1110A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00080 | 80 |  | A17RV1110A_YLH | rot.vlv. RV1110A lime pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 2 | 30 | DI |  |  | C | 12.1.1 | RV1110A lime pneu.convey. - in running |  | RV1110A | A17 | RV | 1110 | A | _ | 11 | YLH | A17RV1110A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00081 | 81 |  | A17RV1110A_YSG | rot.vlv. RV1110A lime pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 3 | 30 | DI |  |  | C | 12.1.1 | RV1110A lime pneu.convey. - supply fault |  | RV1110A | A17 | RV | 1110 | A | _ | 11 | YSG | A17RV1110A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00082 | 82 |  | A17RV1110A_HSH | rot.vlv. RV1110A lime pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 11 | 22 | DO |  |  | C | 12.1.1 | RV1110A lime pneu.convey. - start/stop |  | RV1110A | A17 | RV | 1110 | A | _ | 11 | HSH | A17RV1110A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00083 | 83 |  | A17RV1110B_YLRE | rot.vlv. RV1110B lime pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 1 | 30 | DI |  |  | C | 12.1.2 | RV1110B lime pneu.convey. - in remote |  | RV1110B | A17 | RV | 1110 | B | _ | 11 | YLRE | A17RV1110B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00084 | 84 |  | A17RV1110B_YLH | rot.vlv. RV1110B lime pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 2 | 30 | DI |  |  | C | 12.1.2 | RV1110B lime pneu.convey. - in running |  | RV1110B | A17 | RV | 1110 | B | _ | 11 | YLH | A17RV1110B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00085 | 85 |  | A17RV1110B_YSG | rot.vlv. RV1110B lime pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 3 | 30 | DI |  |  | C | 12.1.2 | RV1110B lime pneu.convey. - supply fault |  | RV1110B | A17 | RV | 1110 | B | _ | 11 | YSG | A17RV1110B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00086 | 86 |  | A17RV1110B_HSH | rot.vlv. RV1110B lime pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 12 | 22 | DO |  |  | C | 12.1.1 | RV1110B lime pneu.convey. - start/stop |  | RV1110B | A17 | RV | 1110 | B | _ | 11 | HSH | A17RV1110B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00087 | 87 |  | A17SOV1304_HSH | vlv. SOV1304 fluid lime compr.air SI1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 1 | 30 | DO |  |  | C | 12.1.6 | SOV1304 fluid lime compr.air SI1100 - open |  | SOV1304 | A17 | SOV | 1304 |  | _ | 11 | HSH | A17SOV1304_HSH | ok | [5 empty] | 0
ID-S01AP1030-00088 | 88 |  | A17SOV1305_HSH | vlv. SOV1305 fluid lime compr.air SI1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 2 | 30 | DO |  |  | C | 12.1.6 | SOV1305 fluid lime compr.air SI1100 - open |  | SOV1305 | A17 | SOV | 1305 |  | _ | 11 | HSH | A17SOV1305_HSH | ok | [5 empty] | 0
ID-S01AP1030-00089 | 89 |  | A17SOV1306A_HSH | vlv. SOV1306A fluid lime compr.air HP1101A - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 3 | 30 | DO |  |  | C | 12.1.6 | SOV1306A fluid lime compr.air HP1101A - open |  | SOV1306A | A17 | SOV | 1306 | A | _ | 12 | HSH | A17SOV1306A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00090 | 90 |  | A17SOV1306B_HSH | vlv. SOV1306B fluid lime compr.air HP1101B - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 4 | 30 | DO |  |  | C | 12.1.6 | SOV1306B fluid lime compr.air HP1101B - open |  | SOV1306B | A17 | SOV | 1306 | B | _ | 12 | HSH | A17SOV1306B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00091 | 91 |  | A17SOV1307A_HSH | vlv. SOV1307A fluid lime compr.air HP1101A - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 5 | 30 | DO |  |  | C | 12.1.6 | SOV1307A fluid lime compr.air HP1101A - open |  | SOV1307A | A17 | SOV | 1307 | A | _ | 12 | HSH | A17SOV1307A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00092 | 92 |  | A17SOV1307B_HSH | vlv. SOV1307B fluid lime compr.air HP1101B - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 6 | 30 | DO |  |  | C | 12.1.6 | SOV1307B fluid lime compr.air HP1101B - open |  | SOV1307B | A17 | SOV | 1307 | B | _ | 12 | HSH | A17SOV1307B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00093 | 93 |  | A17SOV1308A_HSH | vlv. SOV1308A fluid lime compr.air RV1110A - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 7 | 30 | DO |  |  | C | 12.1.6 | SOV1308A fluid lime compr.air RV1110A - open |  | SOV1308A | A17 | SOV | 1308 | A | _ | 12 | HSH | A17SOV1308A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00094 | 94 |  | A17SOV1308B_HSH | vlv. SOV1308B fluid lime compr.air RV1110B - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 8 | 30 | DO |  |  | C | 12.1.6 | SOV1308B fluid lime compr.air RV1110B - open |  | SOV1308B | A17 | SOV | 1308 | B | _ | 12 | HSH | A17SOV1308B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00095 | 95 |  | A17SSL1103A | speed L SSL1103A lime conveyor SW1103A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 6 | 27 | DI |  |  | C | 12.1.5 | L SSL1103A lime conveyor SW1103A |  | L | A17 | SSL | 1103 | A |  |  |  | A17SSL1103A | ok | [5 empty] | 0
ID-S01AP1030-00096 | 96 |  | A17SSL1103B | speed L SSL1103B lime conveyor SW1103B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 6 | 24 | DI |  |  | C | 12.1.6 | L SSL1103B lime conveyor SW1103B |  | L | A17 | SSL | 1103 | B |  |  |  | A17SSL1103B | ok | [5 empty] | 0
ID-S01AP1030-00097 | 97 |  | A17SSL1104A | speed L SSL1104A lime conveyor SW1104A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 7 | 27 | DI |  |  | C | 12.1.5 | L SSL1104A lime conveyor SW1104A |  | L | A17 | SSL | 1104 | A |  |  |  | A17SSL1104A | ok | [5 empty] | 0
ID-S01AP1030-00098 | 98 |  | A17SSL1104B | speed L SSL1104B lime conveyor SW1104B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 7 | 24 | DI |  |  | C | 12.1.6 | L SSL1104B lime conveyor SW1104B |  | L | A17 | SSL | 1104 | B |  |  |  | A17SSL1104B | ok | [5 empty] | 0
ID-S01AP1030-00099 | 99 |  | A17SSL1110A | speed L SSL1110A lime rot.vlv. RV1110A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 8 | 27 | DI |  |  | C | 12.1.5 | L SSL1110A lime rot.vlv. RV1110A |  | L | A17 | SSL | 1110 | A |  |  |  | A17SSL1110A | ok | [5 empty] | 0
ID-S01AP1030-00100 | 100 |  | A17SSL1110B | speed L SSL1110B lime rot.vlv. RV1110B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 5 | 27 | DI |  |  | C | 12.1.6 | L SSL1110B lime rot.vlv. RV1110B |  | L | A17 | SSL | 1110 | B |  |  |  | A17SSL1110B | ok | [5 empty] | 0
ID-S01AP1030-00101 | 101 |  | A17SW1103A_YLRE | screw conv. SW1103A extract. lime - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 4 | 30 | DI |  |  | C | 12.1.1 | conv. SW1103A extract. lime - in remote |  | conv. | A17 | SW | 1103 | A | _ | 11 | YLRE | A17SW1103A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00102 | 102 |  | A17SW1103A_YLH | screw conv. SW1103A extract. lime - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 5 | 30 | DI |  |  | C | 12.1.1 | conv. SW1103A extract. lime - in running |  | conv. | A17 | SW | 1103 | A | _ | 11 | YLH | A17SW1103A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00103 | 103 |  | A17SW1103A_YSG | screw conv. SW1103A extract. lime - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 6 | 30 | DI |  |  | C | 12.1.1 | conv. SW1103A extract. lime - supply fault |  | conv. | A17 | SW | 1103 | A | _ | 11 | YSG | A17SW1103A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00104 | 104 |  | A17SW1103A_HSH | screw conv. SW1103A extract. lime - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 13 | 22 | DO |  |  | C | 12.1.1 | conv. SW1103A extract. lime - start/stop |  | conv. | A17 | SW | 1103 | A | _ | 11 | HSH | A17SW1103A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00105 | 105 |  | A17SW1103B_YLRE | screw conv. SW1103B extract. lime - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 16 | 27 | DI |  |  | C | 12.1.2 | conv. SW1103B extract. lime - in remote |  | conv. | A17 | SW | 1103 | B | _ | 11 | YLRE | A17SW1103B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00106 | 106 |  | A17SW1103B_YLH | screw conv. SW1103B extract. lime - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 17 | 27 | DI |  |  | C | 12.1.2 | conv. SW1103B extract. lime - in running |  | conv. | A17 | SW | 1103 | B | _ | 11 | YLH | A17SW1103B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00107 | 107 |  | A17SW1103B_YSG | screw conv. SW1103B extract. lime - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 18 | 27 | DI |  |  | C | 12.1.2 | conv. SW1103B extract. lime - supply fault |  | conv. | A17 | SW | 1103 | B | _ | 11 | YSG | A17SW1103B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00108 | 108 |  | A17SW1103B_HSH | screw conv. SW1103B extract. lime - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 14 | 22 | DO |  |  | C | 12.1.1 | conv. SW1103B extract. lime - start/stop |  | conv. | A17 | SW | 1103 | B | _ | 11 | HSH | A17SW1103B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00109 | 109 |  | A17SW1104A_YLRE | screw conv. SW1104A dosag. lime - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 7 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. lime - in remote |  | conv. | A17 | SW | 1104 | A | _ | 11 | YLRE | A17SW1104A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00110 | 110 |  | A17SW1104A_YLH | screw conv. SW1104A dosag. lime - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 8 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. lime - in running |  | conv. | A17 | SW | 1104 | A | _ | 11 | YLH | A17SW1104A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00111 | 111 |  | A17SW1104A_YS | screw conv. SW1104A dosag. lime - gen.fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 9 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. lime - gen.fault |  | conv. | A17 | SW | 1104 | A | _ | 11 | YS | A17SW1104A_YS | ok | [5 empty] | 0
ID-S01AP1030-00112 | 112 |  | A17SW1104A_YSG | screw conv. SW1104A dosag. lime - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 10 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. lime - supply fault |  | conv. | A17 | SW | 1104 | A | _ | 11 | YSG | A17SW1104A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00113 | 113 |  | A17SW1104A_HSH | screw conv. SW1104A dosag. lime - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 15 | 22 | DO |  |  | C | 12.1.1 | conv. SW1104A dosag. lime - start/stop |  | conv. | A17 | SW | 1104 | A | _ | 11 | HSH | A17SW1104A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00114 | 114 |  | A17SW1104A_SI | screw conv. SW1104A dosag. lime - speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.7 | 1 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104A dosag. lime - speed |  | conv. | A17 | SW | 1104 | A | _ | 11 | SI | A17SW1104A_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00115 | 115 |  | A17SW1104A_II | screw conv. SW1104A dosag. lime - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 12 |  | 12.1.1.7 | 2 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104A dosag. lime - current |  | conv. | A17 | SW | 1104 | A | _ | 11 | II | A17SW1104A_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1030-00116 | 116 |  | A17SW1104A_SY | screw conv. SW1104A dosag. lime - req.speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.8 | 1 | 8 | AO |  |  | C | 12.1.1 | conv. SW1104A dosag. lime - req.speed |  | conv. | A17 | SW | 1104 | A | _ | 11 | SY | A17SW1104A_SY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00117 | 117 |  | A17SW1104B_YLRE | screw conv. SW1104B dosag. lime - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 19 | 27 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. lime - in remote |  | conv. | A17 | SW | 1104 | B | _ | 11 | YLRE | A17SW1104B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00118 | 118 |  | A17SW1104B_YLH | screw conv. SW1104B dosag. lime - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 20 | 27 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. lime - in running |  | conv. | A17 | SW | 1104 | B | _ | 11 | YLH | A17SW1104B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00119 | 119 |  | A17SW1104B_YS | screw conv. SW1104B dosag. lime - gen.fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 21 | 27 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. lime - gen.fault |  | conv. | A17 | SW | 1104 | B | _ | 11 | YS | A17SW1104B_YS | ok | [5 empty] | 0
ID-S01AP1030-00120 | 120 |  | A17SW1104B_YSG | screw conv. SW1104B dosag. lime - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 22 | 27 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. lime - supply fault |  | conv. | A17 | SW | 1104 | B | _ | 11 | YSG | A17SW1104B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00121 | 121 |  | A17SW1104B_HSH | screw conv. SW1104B dosag. lime - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 16 | 22 | DO |  |  | C | 12.1.1 | conv. SW1104B dosag. lime - start/stop |  | conv. | A17 | SW | 1104 | B | _ | 11 | HSH | A17SW1104B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00122 | 122 |  | A17SW1104B_SI | screw conv. SW1104B dosag. lime - speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.7 | 3 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104B dosag. lime - speed |  | conv. | A17 | SW | 1104 | B | _ | 11 | SI | A17SW1104B_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00123 | 123 |  | A17SW1104B_II | screw conv. SW1104B dosag. lime - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 12 |  | 12.1.1.7 | 4 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104B dosag. lime - current |  | conv. | A17 | SW | 1104 | B | _ | 11 | II | A17SW1104B_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1030-00124 | 124 |  | A17SW1104B_SY | screw conv. SW1104B dosag. lime - req.speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.8 | 2 | 8 | AO |  |  | C | 12.1.1 | conv. SW1104B dosag. lime - req.speed |  | conv. | A17 | SW | 1104 | B | _ | 11 | SY | A17SW1104B_SY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00125 | 125 |  | A17TSH1120 | temp. H TSH1120 lime Heater EH1120 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.7 | 6 | 27 | DI |  |  | C | 12.1.6 | H TSH1120 lime Heater EH1120 |  | H | A17 | TSH | 1120 |  |  |  |  | A17TSH1120 | ok | [5 empty] | 0
ID-S01AP1030-00126 | 126 |  | A17TSH1121A | temp. H TSH1121A lime Heater EH1121A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 9 | 27 | DI |  |  | C | 12.1.5 | H TSH1121A lime Heater EH1121A |  | H | A17 | TSH | 1121 | A |  |  |  | A17TSH1121A | ok | [5 empty] | 0
ID-S01AP1030-00127 | 127 |  | A17TSH1121B | temp. H TSH1121B lime Heater EH1121B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 7 | 27 | DI |  |  | C | 12.1.6 | H TSH1121B lime Heater EH1121B |  | H | A17 | TSH | 1121 | B |  |  |  | A17TSH1121B | ok | [5 empty] | 0
ID-S01AP1030-00128 | 128 |  | A17TSH1122A | temp. H TSH1122A lime Heater EH1122A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 10 | 27 | DI |  |  | C | 12.1.5 | H TSH1122A lime Heater EH1122A |  | H | A17 | TSH | 1122 | A |  |  |  | A17TSH1122A | ok | [5 empty] | 0
ID-S01AP1030-00129 | 129 |  | A17TSH1122B | temp. H TSH1122B lime Heater EH1122B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 8 | 27 | DI |  |  | C | 12.1.6 | H TSH1122B lime Heater EH1122B |  | H | A17 | TSH | 1122 | B |  |  |  | A17TSH1122B | ok | [5 empty] | 0
ID-S01AP1030-00130 | 130 |  | A17TSHH1107A | temp. HH TSHH1107A lime pneu.convey. A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 11 | 27 | DI |  |  | C | 12.1.5 | HH TSHH1107A lime pneu.convey. A |  | HH | A17 | TSHH | 1107 | A |  |  |  | A17TSHH1107A | ok | [5 empty] | 0
ID-S01AP1030-00131 | 131 |  | A17TSHH1107B | temp. HH TSHH1107B lime pneu.convey. B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 9 | 27 | DI |  |  | C | 12.1.6 | HH TSHH1107B lime pneu.convey. B |  | HH | A17 | TSHH | 1107 | B |  |  |  | A17TSHH1107B | ok | [5 empty] | 0
ID-S01AP1030-00132 | 132 |  | A17TI1107A | temp. TT1107A lime pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 12 |  | 12.1.6.2 | 2 | 8 | AI |  |  | C | 12.1.6 | TT1107A lime pneu.convey. |  | TT1107A | A17 | TI | 1107 | A |  |  |  | A17TI1107A | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00133 | 133 |  | A17TI1107B | temp. TT1107B lime pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 12 |  | 12.1.5.7 | 3 | 9 | AI |  |  | C | 12.1.5 | TT1107B lime pneu.convey. |  | TT1107B | A17 | TI | 1107 | B |  |  |  | A17TI1107B | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00134 | 134 |  | A17WI1100 | weight WT1100 lime silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 100 | ton | 220 Vac / .. | 12 |  | 12.1.6.2 | 3 | 8 | AI |  |  | H | 12.1.6 | WT1100 lime silos SL1100 |  | WT1100 | A17 | WI | 1100 |  |  |  |  | A17WI1100 | ok |  |  |  | 0 | 100 | ton
ID-S01AP1030-00135 | 135 |  | A17WI1104A | weight WT1104A lime hopper HP1101A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 600 | kg | 220 Vac / .. | 12 |  | 12.1.6.2 | 4 | 8 | AI |  |  | H | 12.1.6 | WT1104A lime hopper HP1101A |  | WT1104A | A17 | WI | 1104 | A |  |  |  | A17WI1104A | ok |  |  |  | 0 | 600 | kg
ID-S01AP1030-00136 | 136 |  | A17WI1104B | weight WT1104B lime hopper HP1101B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 600 | kg | 220 Vac / .. | 12 |  | 12.1.5.7 | 4 | 9 | AI |  |  | H | 12.1.5 | WT1104B lime hopper HP1101B |  | WT1104B | A17 | WI | 1104 | B |  |  |  | A17WI1104B | ok |  |  |  | 0 | 600 | kg
ID-S01AP1030-00137 | 137 |  | A17ZSH1100 | pos. H ZSH1100 filling lime SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A17 DP01 | CHN1-TDZ2-A17-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.7 | 10 | 27 | DI |  |  | C | 12.1.6 | H ZSH1100 filling lime SL1100 |  | H | A17 | ZSH | 1100 |  |  |  |  | A17ZSH1100 | ok | [5 empty] | 0
ID-S01AP1030-00138 | 138 |  | A18AI1100 | anal. AT1100 sampl. act.carb. CO |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 1000 | ppm | 24Vdc / .. | 12 |  | 12.1.5.6 | 1 | 11 | AI |  |  | C | 12.1.5 | AT1100 sampl. act.carb. CO |  | AT1100 | A18 | AI | 1100 |  |  |  |  | A18AI1100 | ok |  |  |  | 0 | 1000 | ppm
ID-S01AP1030-00139 | 139 |  | A18CK1106A_YLRE | compr. CK1106A act.carb. pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 11 | 30 | DI |  |  | C | 12.1.1 | CK1106A act.carb. pneu.convey. - in remote |  | CK1106A | A18 | CK | 1106 | A | _ | 11 | YLRE | A18CK1106A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00140 | 140 |  | A18CK1106A_YLH | compr. CK1106A act.carb. pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 12 | 30 | DI |  |  | C | 12.1.1 | CK1106A act.carb. pneu.convey. - in running |  | CK1106A | A18 | CK | 1106 | A | _ | 11 | YLH | A18CK1106A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00141 | 141 |  | A18CK1106A_YSG | compr. CK1106A act.carb. pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 13 | 30 | DI |  |  | C | 12.1.1 | CK1106A act.carb. pneu.convey. - supply fault |  | CK1106A | A18 | CK | 1106 | A | _ | 11 | YSG | A18CK1106A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00142 | 142 |  | A18CK1106A_HSH | compr. CK1106A act.carb. pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 17 | 22 | DO |  |  | C | 12.1.1 | CK1106A act.carb. pneu.convey. - start/stop |  | CK1106A | A18 | CK | 1106 | A | _ | 11 | HSH | A18CK1106A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00143 | 143 |  | A18CK1106B_YLRE | compr. CK1106B act.carb. pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 4 | 30 | DI |  |  | C | 12.1.2 | CK1106B act.carb. pneu.convey. - in remote |  | CK1106B | A18 | CK | 1106 | B | _ | 11 | YLRE | A18CK1106B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00144 | 144 |  | A18CK1106B_YLH | compr. CK1106B act.carb. pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 5 | 30 | DI |  |  | C | 12.1.2 | CK1106B act.carb. pneu.convey. - in running |  | CK1106B | A18 | CK | 1106 | B | _ | 11 | YLH | A18CK1106B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00145 | 145 |  | A18CK1106B_YSG | compr. CK1106B act.carb. pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 6 | 30 | DI |  |  | C | 12.1.2 | CK1106B act.carb. pneu.convey. - supply fault |  | CK1106B | A18 | CK | 1106 | B | _ | 11 | YSG | A18CK1106B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00146 | 146 |  | A18CK1106B_HSH | compr. CK1106B act.carb. pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.1.4 | 18 | 22 | DO |  |  | C | 12.1.1 | CK1106B act.carb. pneu.convey. - start/stop |  | CK1106B | A18 | CK | 1106 | B | _ | 11 | HSH | A18CK1106B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00147 | 147 |  | A18FN1105A_YLH | fan FN1105A cooling act.carb. M1104A - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 14 | 30 | DI |  |  | C | 12.1.1 | FN1105A cooling act.carb. M1104A - in running |  | FN1105A | A18 | FN | 1105 | A | _ | 11 | YLH | A18FN1105A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00148 | 148 |  | A18FN1105A_YSG | fan FN1105A cooling act.carb. M1104A - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 15 | 30 | DI |  |  | C | 12.1.1 | FN1105A cooling act.carb. M1104A - supply fault |  | FN1105A | A18 | FN | 1105 | A | _ | 11 | YSG | A18FN1105A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00149 | 149 |  | A18FN1105A_HSH | fan FN1105A cooling act.carb. M1104A - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 10 | 39 | DO |  |  | C | 12.1.2 | FN1105A cooling act.carb. M1104A - start/stop |  | FN1105A | A18 | FN | 1105 | A | _ | 11 | HSH | A18FN1105A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00150 | 150 |  | A18FN1105B_YLH | fan FN1105B cooling act.carb. M1104B - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 23 | 27 | DI |  |  | C | 12.1.2 | FN1105B cooling act.carb. M1104B - in running |  | FN1105B | A18 | FN | 1105 | B | _ | 11 | YLH | A18FN1105B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00151 | 151 |  | A18FN1105B_YSG | fan FN1105B cooling act.carb. M1104B - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 24 | 27 | DI |  |  | C | 12.1.2 | FN1105B cooling act.carb. M1104B - supply fault |  | FN1105B | A18 | FN | 1105 | B | _ | 11 | YSG | A18FN1105B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00152 | 152 |  | A18FN1105B_HSH | fan FN1105B cooling act.carb. M1104B - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 11 | 39 | DO |  |  | C | 12.1.2 | FN1105B cooling act.carb. M1104B - start/stop |  | FN1105B | A18 | FN | 1105 | B | _ | 11 | HSH | A18FN1105B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00153 | 153 |  | A18FSL1106A | flow L FSL1106A act.carb. pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 12 | 27 | DI |  |  | C | 12.1.5 | L FSL1106A act.carb. pneu.convey. |  | L | A18 | FSL | 1106 | A |  |  |  | A18FSL1106A | ok | [5 empty] | 0
ID-S01AP1030-00154 | 154 |  | A18FSL1106B | flow L FSL1106B act.carb. pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 11 | 27 | DI |  |  | C | 12.1.6 | L FSL1106B act.carb. pneu.convey. |  | L | A18 | FSL | 1106 | B |  |  |  | A18FSL1106B | ok | [5 empty] | 0
ID-S01AP1030-00155 | 155 |  | A18HV1101A_ZSH | vlv. HV1101A extract. act.carb. silos SL1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.7.1 | 1 | 18 | DI |  |  | C | 12.1.7 | HV1101A extract. act.carb. silos SL1100 - opened |  | HV1101A | A18 | HV | 1101 | A | _ | 11 | ZSH | A18HV1101A_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00156 | 156 |  | A18HV1101B_ZSH | vlv. HV1101B extract. act.carb. silos SL1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.6 | 8 | 24 | DI |  |  | C | 12.1.6 | HV1101B extract. act.carb. silos SL1100 - opened |  | HV1101B | A18 | HV | 1101 | B | _ | 11 | ZSH | A18HV1101B_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00157 | 157 |  | A18LP1100_YL | loc.pan. LP1100 filling act.carb. SL1100 - reset |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | attivo | 0 |  | 12 |  | 12.1.4.8 | 4 | 26 | DI |  |  | C | 12.1.4 | LP1100 filling act.carb. SL1100 - reset |  | LP1100 | A18 | LP | 1100 |  | _ | 10 | YL | A18LP1100_YL | ok | [5 empty] | 0
ID-S01AP1030-00158 | 158 |  | A18LP11100_YSA | loc.pan. LP1100 filling act.carb. SL1100 - charge alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 6 | 31 | DO |  |  | C | 12.1.4 | LP1100 filling act.carb. SL1100 - charge alarm |  | LP1100 | A18 | LP | 11100 |  | _ | 11 | YSA | A18LP11100_YSA | ok | [5 empty] | 0
ID-S01AP1030-00159 | 159 |  | A18LP11100_YLRE | loc.pan. LP1100 filling act.carb. SL1100 - charge ready |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 7 | 31 | DO |  |  | C | 12.1.4 | LP1100 filling act.carb. SL1100 - charge ready |  | LP1100 | A18 | LP | 11100 |  | _ | 11 | YLRE | A18LP11100_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00160 | 160 |  | A18LP11100_LAHH | loc.pan. LP1100 filling act.carb. SL1100 - visive alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 8 | 31 | DO |  |  | C | 12.1.4 | LP1100 filling act.carb. SL1100 - visive alarm |  | LP1100 | A18 | LP | 11100 |  | _ | 11 | LAHH | A18LP11100_LAHH | ok | [5 empty] | 0
ID-S01AP1030-00161 | 161 |  | A18LP21100_LAHH | loc.pan. LP1100 filling act.carb. SL1100 - acustic alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 9 | 31 | DO |  |  | C | 12.1.4 | LP1100 filling act.carb. SL1100 - acustic alarm |  | LP1100 | A18 | LP | 21100 |  | _ | 11 | LAHH | A18LP21100_LAHH | ok | [5 empty] | 0
ID-S01AP1030-00162 | 162 |  | A18LP11100_LI | loc.pan. LP1100 filling act.carb. SL1100 - Level indicator |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LP1100 filling act.carb. SL1100 - Level indicator |  | LP1100 | A18 | LP | 11100 |  | _ | 11 | LI | A18LP11100_LI | ok | [5 empty] | %
ID-S01AP1030-00163 | 163 |  | A18LP1110_YL | loc.pan. LP1110 earth act.carb. SL1100 - check ok |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | attivo | 0 |  | 12 |  | 12.1.4.8 | 5 | 26 | DI |  |  | C | 12.1.4 | LP1110 earth act.carb. SL1100 - check ok |  | LP1110 | A18 | LP | 1110 |  | _ | 10 | YL | A18LP1110_YL | ok | [5 empty] | 0
ID-S01AP1030-00164 | 164 |  | A18CD1300_YLRE | aut.pan. AP1300 cleaning act.carb. FF1100 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.4.8 | 6 | 26 | DI |  |  | C | 12.1.4 | AP1300 cleaning act.carb. FF1100 - in remote |  | AP1300 | A18 | CD | 1300 |  | _ | 10 | YLRE | A18CD1300_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00165 | 165 |  | A18CD1300_YSA | aut.pan. AP1300 cleaning act.carb. FF1100 - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.4.8 | 7 | 26 | DI |  |  | C | 12.1.4 | AP1300 cleaning act.carb. FF1100 - com.alarm |  | AP1300 | A18 | CD | 1300 |  | _ | 10 | YSA | A18CD1300_YSA | ok | [5 empty] | 0
ID-S01AP1030-00166 | 166 |  | A18CD1300_HSH | aut.pan. AP1300 cleaning act.carb. FF1100 - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 12 |  | 12.1.4.5 | 10 | 31 | DO |  |  | C | 12.1.4 | AP1300 cleaning act.carb. FF1100 - enable |  | AP1300 | A18 | CD | 1300 |  | _ | 10 | HSH | A18CD1300_HSH | ok | [5 empty] | 0
ID-S01AP1030-00167 | 167 |  | A18LSH1101A | lev. H LSH1101A act.carb. hopper HP1101A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | A | 12.1.7.1 | 2 | 18 | DI |  |  | D | 12.1.7 | H LSH1101A act.carb. hopper HP1101A |  | H | A18 | LSH | 1101 | A |  |  |  | A18LSH1101A | ok | [5 empty] | 0
ID-S01AP1030-00168 | 168 |  | A18LSH1101B | lev. H LSH1101B act.carb. hopper HP1101B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 9 | 24 | DI |  |  | D | 12.1.6 | H LSH1101B act.carb. hopper HP1101B |  | H | A18 | LSH | 1101 | B |  |  |  | A18LSH1101B | ok | [5 empty] | 0
ID-S01AP1030-00169 | 169 |  | A18LSHH1100 | lev. HH LSHH1100 act.carb. silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.7.1 | 3 | 18 | DI |  |  | D | 12.1.7 | HH LSHH1100 act.carb. silos SL1100 |  | HH | A18 | LSHH | 1100 |  |  |  |  | A18LSHH1100 | ok | [5 empty] | 0
ID-S01AP1030-00170 | 170 |  | A18LSL1101A | lev. L LSL1101A act.carb. hopper HP1101A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | A | 12.1.7.1 | 4 | 18 | DI |  |  | D | 12.1.7 | L LSL1101A act.carb. hopper HP1101A |  | L | A18 | LSL | 1101 | A |  |  |  | A18LSL1101A | ok | [5 empty] | 0
ID-S01AP1030-00171 | 171 |  | A18LSL1101B | lev. L LSL1101B act.carb. hopper HP1101B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 10 | 24 | DI |  |  | D | 12.1.6 | L LSL1101B act.carb. hopper HP1101B |  | L | A18 | LSL | 1101 | B |  |  |  | A18LSL1101B | ok | [5 empty] | 0
ID-S01AP1030-00172 | 172 |  | A18LSLL1100 | lev. LL LSLL1100 act.carb. silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.7.1 | 5 | 18 | DI |  |  | D | 12.1.7 | LL LSLL1100 act.carb. silos SL1100 |  | LL | A18 | LSLL | 1100 |  |  |  |  | A18LSLL1100 | ok | [5 empty] | 0
ID-S01AP1030-00173 | 173 |  | A18LI1100 | lev. LT1100 act.carb. silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LT1100 act.carb. silos SL1100 |  | LT1100 | A18 | LI | 1100 |  |  |  |  | A18LI1100 | ok | [5 empty] | %
ID-S01AP1030-00174 | 174 |  | A18POV1100_ZSL | vlv. POV1100 filling act.carb. silos SL1100 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.1 | 6 | 18 | DI |  |  | C | 12.1.7 | POV1100 filling act.carb. silos SL1100 - closed |  | POV1100 | A18 | POV | 1100 |  | _ | 11 | ZSL | A18POV1100_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00175 | 175 |  | A18POV1100_HSH | vlv. POV1100 filling act.carb. silos SL1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 9 | 30 | DO |  |  | C | 12.1.6 | POV1100 filling act.carb. silos SL1100 - open |  | POV1100 | A18 | POV | 1100 |  | _ | 11 | HSH | A18POV1100_HSH | ok | [5 empty] | 0
ID-S01AP1030-00176 | 176 |  | A18POV1102A_ZSH | vlv. POV1102A extract. act.carb. silos SL1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.7.1 | 7 | 18 | DI |  |  | C | 12.1.7 | POV1102A extract. act.carb. silos SL1100 - opened |  | POV1102A | A18 | POV | 1102 | A | _ | 12 | ZSH | A18POV1102A_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00177 | 177 |  | A18POV1102A_HSH | vlv. POV1102A extract. act.carb. silos SL1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | A18LP1102 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.1.4 | 19 | 22 | DO |  |  | C | 12.1.1 | POV1102A extract. act.carb. silos SL1100 - open |  | POV1102A | A18 | POV | 1102 | A | _ | 12 | HSH | A18POV1102A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00178 | 178 |  | A18POV1102A_HSL | vlv. POV1102A extract. act.carb. silos SL1100 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | A18LP1102 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.1.4 | 20 | 22 | DO |  |  | C | 12.1.1 | POV1102A extract. act.carb. silos SL1100 - close |  | POV1102A | A18 | POV | 1102 | A | _ | 12 | HSL | A18POV1102A_HSL | ok | [5 empty] | 0
ID-S01AP1030-00179 | 179 |  | A18POV1102B_ZSH | vlv. POV1102B extract. act.carb. silos SL1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.6 | 11 | 24 | DI |  |  | C | 12.1.6 | POV1102B extract. act.carb. silos SL1100 - opened |  | POV1102B | A18 | POV | 1102 | B | _ | 12 | ZSH | A18POV1102B_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00180 | 180 |  | A18POV1102B_HSH | vlv. POV1102B extract. act.carb. silos SL1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | A18LP1102 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.1.4 | 21 | 22 | DO |  |  | C | 12.1.1 | POV1102B extract. act.carb. silos SL1100 - open |  | POV1102B | A18 | POV | 1102 | B | _ | 12 | HSH | A18POV1102B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00181 | 181 |  | A18POV1102B_HSL | vlv. POV1102B extract. act.carb. silos SL1100 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | A18LP1102 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.1.4 | 22 | 22 | DO |  |  | C | 12.1.1 | POV1102B extract. act.carb. silos SL1100 - close |  | POV1102B | A18 | POV | 1102 | B | _ | 12 | HSL | A18POV1102B_HSL | ok | [5 empty] | 0
ID-S01AP1030-00182 | 182 |  | A18PSHH1100 | pres. HH PSHH1100 act.carb. compr.air FF1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.7.1 | 8 | 18 | DI |  |  | C | 12.1.7 | HH PSHH1100 act.carb. compr.air FF1100 |  | HH | A18 | PSHH | 1100 |  |  |  |  | A18PSHH1100 | ok | [5 empty] | 0
ID-S01AP1030-00183 | 183 |  | A18PSL1301 | pres. L PSL1301 act.carb. compr.air PRV1301 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.7.1 | 9 | 18 | DI |  |  | C | 12.1.7 | L PSL1301 act.carb. compr.air PRV1301 |  | L | A18 | PSL | 1301 |  |  |  |  | A18PSL1301 | ok | [5 empty] | 0
ID-S01AP1030-00184 | 184 |  | A18PSL1307 | pres. L PSL1307 act.carb. Nitrogen gas |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.7 | 12 | 27 | DI |  |  | C | 12.1.6 | L PSL1307 act.carb. Nitrogen gas |  | L | A18 | PSL | 1307 |  |  |  |  | A18PSL1307 | ok | [5 empty] | 0
ID-S01AP1030-00185 | 185 |  | A18PI1106A | press. PT1106A act.carb. pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 4000 | mmH20 |  | 12 |  | 12.1.5.7 | 5 | 9 | AI |  |  | C | 12.1.5 | PT1106A act.carb. pneu.convey. |  | PT1106A | A18 | PI | 1106 | A |  |  |  | A18PI1106A | ok |  |  |  | 0 | 4000 | mmH20
ID-S01AP1030-00186 | 186 |  | A18PI1106B | press. PT1106B act.carb. pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 4000 | mmH20 |  | 12 |  | 12.1.5.7 | 6 | 9 | AI |  |  | C | 12.1.5 | PT1106B act.carb. pneu.convey. |  | PT1106B | A18 | PI | 1106 | B |  |  |  | A18PI1106B | ok |  |  |  | 0 | 4000 | mmH20
ID-S01AP1030-00187 | 187 |  | A18RV1107A_YLRE | rot.vlv. RV1107A act.carb. pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 16 | 30 | DI |  |  | C | 12.1.1 | RV1107A act.carb. pneu.convey. - in remote |  | RV1107A | A18 | RV | 1107 | A | _ | 11 | YLRE | A18RV1107A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00188 | 188 |  | A18RV1107A_YLH | rot.vlv. RV1107A act.carb. pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 17 | 30 | DI |  |  | C | 12.1.1 | RV1107A act.carb. pneu.convey. - in running |  | RV1107A | A18 | RV | 1107 | A | _ | 11 | YLH | A18RV1107A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00189 | 189 |  | A18RV1107A_YSG | rot.vlv. RV1107A act.carb. pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 18 | 30 | DI |  |  | C | 12.1.1 | RV1107A act.carb. pneu.convey. - supply fault |  | RV1107A | A18 | RV | 1107 | A | _ | 11 | YSG | A18RV1107A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00190 | 190 |  | A18RV1107A_HSH | rot.vlv. RV1107A act.carb. pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 12 | 39 | DO |  |  | C | 12.1.2 | RV1107A act.carb. pneu.convey. - start/stop |  | RV1107A | A18 | RV | 1107 | A | _ | 11 | HSH | A18RV1107A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00191 | 191 |  | A18RV1107B_YLRE | rot.vlv. RV1107B act.carb. pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 25 | 27 | DI |  |  | C | 12.1.2 | RV1107B act.carb. pneu.convey. - in remote |  | RV1107B | A18 | RV | 1107 | B | _ | 11 | YLRE | A18RV1107B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00192 | 192 |  | A18RV1107B_YLH | rot.vlv. RV1107B act.carb. pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.8 | 26 | 27 | DI |  |  | C | 12.1.2 | RV1107B act.carb. pneu.convey. - in running |  | RV1107B | A18 | RV | 1107 | B | _ | 11 | YLH | A18RV1107B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00193 | 193 |  | A18RV1107B_YSG | rot.vlv. RV1107B act.carb. pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.8 | 27 | 27 | DI |  |  | C | 12.1.2 | RV1107B act.carb. pneu.convey. - supply fault |  | RV1107B | A18 | RV | 1107 | B | _ | 11 | YSG | A18RV1107B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00194 | 194 |  | A18RV1107B_HSH | rot.vlv. RV1107B act.carb. pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 13 | 39 | DO |  |  | C | 12.1.2 | RV1107B act.carb. pneu.convey. - start/stop |  | RV1107B | A18 | RV | 1107 | B | _ | 11 | HSH | A18RV1107B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00195 | 195 |  | A18SOV1304_HSH | vlv. SOV1304 fluid act.carb. compr.air SI1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 10 | 30 | DO |  |  | C | 12.1.6 | SOV1304 fluid act.carb. compr.air SI1100 - open |  | SOV1304 | A18 | SOV | 1304 |  | _ | 11 | HSH | A18SOV1304_HSH | ok | [5 empty] | 0
ID-S01AP1030-00196 | 196 |  | A18SOV1305_HSH | vlv. SOV1305 fluid act.carb. compr.air SI1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 11 | 30 | DO |  |  | C | 12.1.6 | SOV1305 fluid act.carb. compr.air SI1100 - open |  | SOV1305 | A18 | SOV | 1305 |  | _ | 11 | HSH | A18SOV1305_HSH | ok | [5 empty] | 0
ID-S01AP1030-00197 | 197 |  | A18SOV1306A_HSH | vlv. SOV1306A fluid act.carb. compr.air HP1101A - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.8.5 | 1 | 2 | DO |  |  | C | 12.1.8 | SOV1306A fluid act.carb. compr.air HP1101A - open |  | SOV1306A | A18 | SOV | 1306 | A | _ | 12 | HSH | A18SOV1306A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00198 | 198 |  | A18SOV1306B_HSH | vlv. SOV1306B fluid act.carb. compr.air HP1101B - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.8.5 | 2 | 2 | DO |  |  | C | 12.1.8 | SOV1306B fluid act.carb. compr.air HP1101B - open |  | SOV1306B | A18 | SOV | 1306 | B | _ | 12 | HSH | A18SOV1306B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00199 | 199 |  | A18SOV1307_HSH | vlv. SOV1307 inert act.carb. nitrog. SI1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBD-1-003 |  | S01AP1030 |  |  |  |  | DOS | RELAY - 24 Vac | true | → | active | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | SOV1307 inert act.carb. nitrog. SI1100 - open |  | SOV1307 | A18 | SOV | 1307 |  | _ | 11 | HSH | A18SOV1307_HSH | ok | [5 empty] | 0
ID-S01AP1030-00200 | 200 |  | A18SSL1103A | speed L SSL1103A act.carb. conveyor SW1103A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.7.1 | 10 | 18 | DI |  |  | C | 12.1.7 | L SSL1103A act.carb. conveyor SW1103A |  | L | A18 | SSL | 1103 | A |  |  |  | A18SSL1103A | ok | [5 empty] | 0
ID-S01AP1030-00201 | 201 |  | A18SSL1103B | speed L SSL1103B act.carb. conveyor SW1103B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 12 | 24 | DI |  |  | C | 12.1.6 | L SSL1103B act.carb. conveyor SW1103B |  | L | A18 | SSL | 1103 | B |  |  |  | A18SSL1103B | ok | [5 empty] | 0
ID-S01AP1030-00202 | 202 |  | A18SSL1104A | speed L SSL1104A act.carb. conveyor SW1104A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.7.1 | 11 | 18 | DI |  |  | C | 12.1.7 | L SSL1104A act.carb. conveyor SW1104A |  | L | A18 | SSL | 1104 | A |  |  |  | A18SSL1104A | ok | [5 empty] | 0
ID-S01AP1030-00203 | 203 |  | A18SSL1104B | speed L SSL1104B act.carb. conveyor SW1104B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 13 | 24 | DI |  |  | C | 12.1.6 | L SSL1104B act.carb. conveyor SW1104B |  | L | A18 | SSL | 1104 | B |  |  |  | A18SSL1104B | ok | [5 empty] | 0
ID-S01AP1030-00204 | 204 |  | A18SSL1107A | speed L SSL1107A act.carb. rot.vlv. RV1107A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.7.1 | 12 | 18 | DI |  |  | C | 12.1.7 | L SSL1107A act.carb. rot.vlv. RV1107A |  | L | A18 | SSL | 1107 | A |  |  |  | A18SSL1107A | ok | [5 empty] | 0
ID-S01AP1030-00205 | 205 |  | A18SSL1107B | speed L SSL1107B act.carb. rot.vlv. RV1107B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 14 | 24 | DI |  |  | C | 12.1.6 | L SSL1107B act.carb. rot.vlv. RV1107B |  | L | A18 | SSL | 1107 | B |  |  |  | A18SSL1107B | ok | [5 empty] | 0
ID-S01AP1030-00206 | 206 |  | A18SW1103A_YLRE | screw conv. SW1103A extract. act.carb. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 19 | 30 | DI |  |  | C | 12.1.1 | conv. SW1103A extract. act.carb. - in remote |  | conv. | A18 | SW | 1103 | A | _ | 11 | YLRE | A18SW1103A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00207 | 207 |  | A18SW1103A_YLH | screw conv. SW1103A extract. act.carb. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 20 | 30 | DI |  |  | C | 12.1.1 | conv. SW1103A extract. act.carb. - in running |  | conv. | A18 | SW | 1103 | A | _ | 11 | YLH | A18SW1103A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00208 | 208 |  | A18SW1103A_YSG | screw conv. SW1103A extract. act.carb. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 21 | 30 | DI |  |  | C | 12.1.1 | conv. SW1103A extract. act.carb. - supply fault |  | conv. | A18 | SW | 1103 | A | _ | 11 | YSG | A18SW1103A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00209 | 209 |  | A18SW1103A_HSH | screw conv. SW1103A extract. act.carb. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 14 | 39 | DO |  |  | C | 12.1.2 | conv. SW1103A extract. act.carb. - start/stop |  | conv. | A18 | SW | 1103 | A | _ | 11 | HSH | A18SW1103A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00210 | 210 |  | A18SW1103B_YLRE | screw conv. SW1103B extract. act.carb. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 7 | 30 | DI |  |  | C | 12.1.2 | conv. SW1103B extract. act.carb. - in remote |  | conv. | A18 | SW | 1103 | B | _ | 11 | YLRE | A18SW1103B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00211 | 211 |  | A18SW1103B_YLH | screw conv. SW1103B extract. act.carb. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 8 | 30 | DI |  |  | C | 12.1.2 | conv. SW1103B extract. act.carb. - in running |  | conv. | A18 | SW | 1103 | B | _ | 11 | YLH | A18SW1103B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00212 | 212 |  | A18SW1103B_YSG | screw conv. SW1103B extract. act.carb. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 9 | 30 | DI |  |  | C | 12.1.2 | conv. SW1103B extract. act.carb. - supply fault |  | conv. | A18 | SW | 1103 | B | _ | 11 | YSG | A18SW1103B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00213 | 213 |  | A18SW1103B_HSH | screw conv. SW1103B extract. act.carb. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 15 | 39 | DO |  |  | C | 12.1.2 | conv. SW1103B extract. act.carb. - start/stop |  | conv. | A18 | SW | 1103 | B | _ | 11 | HSH | A18SW1103B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00214 | 214 |  | A18SW1104A_YLRE | screw conv. SW1104A dosag. act.carb. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 22 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. act.carb. - in remote |  | conv. | A18 | SW | 1104 | A | _ | 11 | YLRE | A18SW1104A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00215 | 215 |  | A18SW1104A_YLH | screw conv. SW1104A dosag. act.carb. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 23 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. act.carb. - in running |  | conv. | A18 | SW | 1104 | A | _ | 11 | YLH | A18SW1104A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00216 | 216 |  | A18SW1104A_YS | screw conv. SW1104A dosag. act.carb. - gen.fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 24 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. act.carb. - gen.fault |  | conv. | A18 | SW | 1104 | A | _ | 11 | YS | A18SW1104A_YS | ok | [5 empty] | 0
ID-S01AP1030-00217 | 217 |  | A18SW1104A_YSG | screw conv. SW1104A dosag. act.carb. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 25 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. act.carb. - supply fault |  | conv. | A18 | SW | 1104 | A | _ | 11 | YSG | A18SW1104A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00218 | 218 |  | A18SW1104A_HSH | screw conv. SW1104A dosag. act.carb. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 16 | 39 | DO |  |  | C | 12.1.2 | conv. SW1104A dosag. act.carb. - start/stop |  | conv. | A18 | SW | 1104 | A | _ | 11 | HSH | A18SW1104A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00219 | 219 |  | A18SW1104A_SI | screw conv. SW1104A dosag. act.carb. - speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.7 | 5 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104A dosag. act.carb. - speed |  | conv. | A18 | SW | 1104 | A | _ | 11 | SI | A18SW1104A_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00220 | 220 |  | A18SW1104A_II | screw conv. SW1104A dosag. act.carb. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 12 |  | 12.1.1.7 | 6 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104A dosag. act.carb. - current |  | conv. | A18 | SW | 1104 | A | _ | 11 | II | A18SW1104A_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1030-00221 | 221 |  | A18SW1104A_SY | screw conv. SW1104A dosag. act.carb. - req.speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.8 | 3 | 8 | AO |  |  | C | 12.1.1 | conv. SW1104A dosag. act.carb. - req.speed |  | conv. | A18 | SW | 1104 | A | _ | 11 | SY | A18SW1104A_SY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00222 | 222 |  | A18SW1104B_YLRE | screw conv. SW1104B dosag. act.carb. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 10 | 30 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. act.carb. - in remote |  | conv. | A18 | SW | 1104 | B | _ | 11 | YLRE | A18SW1104B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00223 | 223 |  | A18SW1104B_YLH | screw conv. SW1104B dosag. act.carb. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 11 | 30 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. act.carb. - in running |  | conv. | A18 | SW | 1104 | B | _ | 11 | YLH | A18SW1104B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00224 | 224 |  | A18SW1104B_YS | screw conv. SW1104B dosag. act.carb. - gen.fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 12 | 30 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. act.carb. - gen.fault |  | conv. | A18 | SW | 1104 | B | _ | 11 | YS | A18SW1104B_YS | ok | [5 empty] | 0
ID-S01AP1030-00225 | 225 |  | A18SW1104B_YSG | screw conv. SW1104B dosag. act.carb. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 13 | 30 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. act.carb. - supply fault |  | conv. | A18 | SW | 1104 | B | _ | 11 | YSG | A18SW1104B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00226 | 226 |  | A18SW1104B_HSH | screw conv. SW1104B dosag. act.carb. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 17 | 39 | DO |  |  | C | 12.1.2 | conv. SW1104B dosag. act.carb. - start/stop |  | conv. | A18 | SW | 1104 | B | _ | 11 | HSH | A18SW1104B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00227 | 227 |  | A18SW1104B_SI | screw conv. SW1104B dosag. act.carb. - speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.7 | 7 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104B dosag. act.carb. - speed |  | conv. | A18 | SW | 1104 | B | _ | 11 | SI | A18SW1104B_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00228 | 228 |  | A18SW1104B_II | screw conv. SW1104B dosag. act.carb. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 12 |  | 12.1.1.7 | 8 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104B dosag. act.carb. - current |  | conv. | A18 | SW | 1104 | B | _ | 11 | II | A18SW1104B_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1030-00229 | 229 |  | A18SW1104B_SY | screw conv. SW1104B dosag. act.carb. - req.speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.8 | 4 | 8 | AO |  |  | C | 12.1.1 | conv. SW1104B dosag. act.carb. - req.speed |  | conv. | A18 | SW | 1104 | B | _ | 11 | SY | A18SW1104B_SY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00230 | 230 |  | A18TI1100 | temp. TT11100 filling act.carb. SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 12 |  | 12.1.5.6 | 2 | 11 | AI |  |  | C | 12.1.5 | TT11100 filling act.carb. SL1100 |  | TT11100 | A18 | TI | 1100 |  |  |  |  | A18TI1100 | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00231 | 231 |  | A18TI1101 | temp. TT11101 filling act.carb. SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 12 |  | 12.1.5.6 | 3 | 11 | AI |  |  | C | 12.1.5 | TT11101 filling act.carb. SL1100 |  | TT11101 | A18 | TI | 1101 |  |  |  |  | A18TI1101 | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00232 | 232 |  | A18TI1102 | temp. TT11102 act.carb. silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT11102 act.carb. silos SL1100 |  | TT11102 | A18 | TI | 1102 |  |  |  |  | A18TI1102 | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00233 | 233 |  | A18TI1103 | temp. TT11103 act.carb. silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT11103 act.carb. silos SL1100 |  | TT11103 | A18 | TI | 1103 |  |  |  |  | A18TI1103 | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00234 | 234 |  | A18WI1100 | weight WT1100 act.carb. silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 50 | ton | 220 Vac / .. | 12 |  | 12.1.5.7 | 7 | 9 | AI |  |  | H | 12.1.5 | WT1100 act.carb. silos SL1100 |  | WT1100 | A18 | WI | 1100 |  |  |  |  | A18WI1100 | ok |  |  |  | 0 | 50 | ton
ID-S01AP1030-00235 | 235 |  | A18WI1104A | weight WT1104A act.carb. hopper HP1101A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 600 | kg | 220 Vac / .. | 12 |  | 12.1.5.7 | 8 | 9 | AI |  |  | H | 12.1.5 | WT1104A act.carb. hopper HP1101A |  | WT1104A | A18 | WI | 1104 | A |  |  |  | A18WI1104A | ok |  |  |  | 0 | 600 | kg
ID-S01AP1030-00236 | 236 |  | A18WI1104B | weight WT1104B act.carb. hopper HP1101B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A17-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 600 | kg | 220 Vac / .. | 12 |  | 12.1.5.7 | 9 | 9 | AI |  |  | H | 12.1.5 | WT1104B act.carb. hopper HP1101B |  | WT1104B | A18 | WI | 1104 | B |  |  |  | A18WI1104B | ok |  |  |  | 0 | 600 | kg
ID-S01AP1030-00237 | 237 |  | A18ZSH1100 | pos. H ZSH1100 filling act.carb. SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A18 DP01 | CHN1-TDZ2-A18-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.7.1 | 13 | 18 | DI |  |  | C | 12.1.7 | H ZSH1100 filling act.carb. SL1100 |  | H | A18 | ZSH | 1100 |  |  |  |  | A18ZSH1100 | ok | [5 empty] | 0
ID-S01AP1030-00238 | 238 |  | A19CY1155_YLRE | conveyor CY1155 dolomia to EL1156 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 |  |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | CY1155 dolomia to EL1156 - in remote |  | CY1155 | A19 | CY | 1155 |  | _ | 10 | YLRE | A19CY1155_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00239 | 239 |  | A19CY1155_YLH | conveyor CY1155 dolomia to EL1156 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 |  |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | CY1155 dolomia to EL1156 - in running |  | CY1155 | A19 | CY | 1155 |  | _ | 10 | YLH | A19CY1155_YLH | ok | [5 empty] | 0
ID-S01AP1030-00240 | 240 |  | A19CY1155_YSG | conveyor CY1155 dolomia to EL1156 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 |  |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | CY1155 dolomia to EL1156 - supply fault |  | CY1155 | A19 | CY | 1155 |  | _ | 10 | YSG | A19CY1155_YSG | ok | [5 empty] | 0
ID-S01AP1030-00241 | 241 |  | A19CY1155_HSH | conveyor CY1155 dolomia to EL1156 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 |  |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | CY1155 dolomia to EL1156 - start/stop |  | CY1155 | A19 | CY | 1155 |  | _ | 10 | HSH | A19CY1155_HSH | ok | [5 empty] | 0
ID-S01AP1030-00242 | 242 |  | A19CK1106A_YLRE | compr. CK1106A dolomia pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 26 | 30 | DI |  |  | C | 12.1.1 | CK1106A dolomia pneu.convey. - in remote |  | CK1106A | A19 | CK | 1106 | A | _ | 11 | YLRE | A19CK1106A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00243 | 243 |  | A19CK1106A_YLH | compr. CK1106A dolomia pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 27 | 30 | DI |  |  | C | 12.1.1 | CK1106A dolomia pneu.convey. - in running |  | CK1106A | A19 | CK | 1106 | A | _ | 11 | YLH | A19CK1106A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00244 | 244 |  | A19CK1106A_YSG | compr. CK1106A dolomia pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 28 | 30 | DI |  |  | C | 12.1.1 | CK1106A dolomia pneu.convey. - supply fault |  | CK1106A | A19 | CK | 1106 | A | _ | 11 | YSG | A19CK1106A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00245 | 245 |  | A19CK1106A_HSH | compr. CK1106A dolomia pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 18 | 39 | DO |  |  | C | 12.1.2 | CK1106A dolomia pneu.convey. - start/stop |  | CK1106A | A19 | CK | 1106 | A | _ | 11 | HSH | A19CK1106A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00246 | 246 |  | A19CK1106B_YLRE | compr. CK1106B dolomia pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 14 | 30 | DI |  |  | C | 12.1.2 | CK1106B dolomia pneu.convey. - in remote |  | CK1106B | A19 | CK | 1106 | B | _ | 11 | YLRE | A19CK1106B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00247 | 247 |  | A19CK1106B_YLH | compr. CK1106B dolomia pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 15 | 30 | DI |  |  | C | 12.1.2 | CK1106B dolomia pneu.convey. - in running |  | CK1106B | A19 | CK | 1106 | B | _ | 11 | YLH | A19CK1106B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00248 | 248 |  | A19CK1106B_YSG | compr. CK1106B dolomia pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 16 | 30 | DI |  |  | C | 12.1.2 | CK1106B dolomia pneu.convey. - supply fault |  | CK1106B | A19 | CK | 1106 | B | _ | 11 | YSG | A19CK1106B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00249 | 249 |  | A19CK1106B_HSH | compr. CK1106B dolomia pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 19 | 39 | DO |  |  | C | 12.1.2 | CK1106B dolomia pneu.convey. - start/stop |  | CK1106B | A19 | CK | 1106 | B | _ | 11 | HSH | A19CK1106B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00250 | 250 |  | A19FN1105A_YLH | fan FN1105Acooling dolomia M1104A - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.1 | 29 | 30 | DI |  |  | C | 12.1.1 | FN1105Acooling dolomia M1104A - in running |  | FN1105Acooling | A19 | FN | 1105 | A | _ | 11 | YLH | A19FN1105A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00251 | 251 |  | A19FN1105A_YSG | fan FN1105Acooling dolomia M1104A - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.1 | 30 | 30 | DI |  |  | C | 12.1.1 | FN1105Acooling dolomia M1104A - supply fault |  | FN1105Acooling | A19 | FN | 1105 | A | _ | 11 | YSG | A19FN1105A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00252 | 252 |  | A19FN1105A_HSH | fan FN1105Acooling dolomia M1104A - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 20 | 39 | DO |  |  | C | 12.1.2 | FN1105Acooling dolomia M1104A - start/stop |  | FN1105Acooling | A19 | FN | 1105 | A | _ | 11 | HSH | A19FN1105A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00253 | 253 |  | A19FN1105B_YLH | fan FN1105Acooling dolomia M1104B - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 17 | 30 | DI |  |  | C | 12.1.2 | FN1105Acooling dolomia M1104B - in running |  | FN1105Acooling | A19 | FN | 1105 | B | _ | 11 | YLH | A19FN1105B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00254 | 254 |  | A19FN1105B_YSG | fan FN1105Acooling dolomia M1104B - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 18 | 30 | DI |  |  | C | 12.1.2 | FN1105Acooling dolomia M1104B - supply fault |  | FN1105Acooling | A19 | FN | 1105 | B | _ | 11 | YSG | A19FN1105B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00255 | 255 |  | A19FN1105B_HSH | fan FN1105Acooling dolomia M1104B - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 21 | 39 | DO |  |  | C | 12.1.2 | FN1105Acooling dolomia M1104B - start/stop |  | FN1105Acooling | A19 | FN | 1105 | B | _ | 11 | HSH | A19FN1105B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00256 | 256 |  | A19FSL1106A | flow L FSL1106A dolomia pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.7.1 | 14 | 18 | DI |  |  | C | 12.1.7 | L FSL1106A dolomia pneu.convey. |  | L | A19 | FSL | 1106 | A |  |  |  | A19FSL1106A | ok | [5 empty] | 0
ID-S01AP1030-00257 | 257 |  | A19FSL1106B | flow L FSL1106B dolomia pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.8.6 | 1 | 17 | DI |  |  | C | 12.1.8 | L FSL1106B dolomia pneu.convey. |  | L | A19 | FSL | 1106 | B |  |  |  | A19FSL1106B | ok | [5 empty] | 0
ID-S01AP1030-00258 | 258 |  | A19HV1101A_ZSH | vlv. HV1101 extract. dolomia silos SL1100A - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.7.1 | 15 | 18 | DI |  |  | C | 12.1.7 | HV1101 extract. dolomia silos SL1100A - opened |  | HV1101 | A19 | HV | 1101 | A | _ | 11 | ZSH | A19HV1101A_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00259 | 259 |  | A19HV1101B_ZSH | vlv. HV1151 extract. dolomia silos SL1100B - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.8.6 | 2 | 17 | DI |  |  | C | 12.1.8 | HV1151 extract. dolomia silos SL1100B - opened |  | HV1151 | A19 | HV | 1101 | B | _ | 11 | ZSH | A19HV1101B_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00260 | 260 |  | A19LP1100A_YL | loc.pan. LP1100A filling dolomia SL1100A - reset |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | attivo | 0 |  | 12 | A | 12.1.3.1 | 1 | 29 | DI |  |  | C | 12.1.3 | LP1100A filling dolomia SL1100A - reset |  | LP1100A | A19 | LP | 1100 | A | _ | 11 | YL | A19LP1100A_YL | ok | [5 empty] | 0
ID-S01AP1030-00261 | 261 |  | A19LP11100A_YSA | loc.pan. LP1100A filling dolomia SL1100A - charge alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 11 | 31 | DO |  |  | C | 12.1.4 | LP1100A filling dolomia SL1100A - charge alarm |  | LP1100A | A19 | LP | 11100 | A | _ | 12 | YSA | A19LP11100A_YSA | ok | [5 empty] | 0
ID-S01AP1030-00262 | 262 |  | A19LP11100A_YLRE | loc.pan. LP1100A filling dolomia SL1100A - charge ready |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 12 | 31 | DO |  |  | C | 12.1.4 | LP1100A filling dolomia SL1100A - charge ready |  | LP1100A | A19 | LP | 11100 | A | _ | 12 | YLRE | A19LP11100A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00263 | 263 |  | A19LP11100A_LAHH | loc.pan. LP1100A filling dolomia SL1100A - visive alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 13 | 31 | DO |  |  | C | 12.1.4 | LP1100A filling dolomia SL1100A - visive alarm |  | LP1100A | A19 | LP | 11100 | A | _ | 12 | LAHH | A19LP11100A_LAHH | ok | [5 empty] | 0
ID-S01AP1030-00264 | 264 |  | A19LP21100A_LAHH | loc.pan. LP1100A filling dolomia SL1100A - acustic alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 14 | 31 | DO |  |  | C | 12.1.4 | LP1100A filling dolomia SL1100A - acustic alarm |  | LP1100A | A19 | LP | 21100 | A | _ | 12 | LAHH | A19LP21100A_LAHH | ok | [5 empty] | 0
ID-S01AP1030-00265 | 265 |  | A19LP11100_LI | loc.pan. LP1100 filling dolomia SL1100 - Level indicator |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LP1100 filling dolomia SL1100 - Level indicator |  | LP1100 | A19 | LP | 11100 |  | _ | 11 | LI | A19LP11100_LI | ok | [5 empty] | %
ID-S01AP1030-00266 | 266 |  | A19LP1100B_YL | loc.pan. LP1100B filling dolomia SL1100B - reset |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | attivo | 0 |  | 12 | B | 12.1.4.8 | 8 | 26 | DI |  |  | C | 12.1.4 | LP1100B filling dolomia SL1100B - reset |  | LP1100B | A19 | LP | 1100 | B | _ | 11 | YL | A19LP1100B_YL | ok | [5 empty] | 0
ID-S01AP1030-00267 | 267 |  | A19LP11100B_YSA | loc.pan. LP1100B filling dolomia SL1100B - charge alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 15 | 31 | DO |  |  | C | 12.1.4 | LP1100B filling dolomia SL1100B - charge alarm |  | LP1100B | A19 | LP | 11100 | B | _ | 12 | YSA | A19LP11100B_YSA | ok | [5 empty] | 0
ID-S01AP1030-00268 | 268 |  | A19LP11100B_YLRE | loc.pan. LP1100B filling dolomia SL1100B - charge ready |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 16 | 31 | DO |  |  | C | 12.1.4 | LP1100B filling dolomia SL1100B - charge ready |  | LP1100B | A19 | LP | 11100 | B | _ | 12 | YLRE | A19LP11100B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00269 | 269 |  | A19LP11100B_LAHH | loc.pan. LP1100B filling dolomia SL1100B - visive alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 17 | 31 | DO |  |  | C | 12.1.4 | LP1100B filling dolomia SL1100B - visive alarm |  | LP1100B | A19 | LP | 11100 | B | _ | 12 | LAHH | A19LP11100B_LAHH | ok | [5 empty] | 0
ID-S01AP1030-00270 | 270 |  | A19LP21100B_LAHH | loc.pan. LP1100B filling dolomia SL1100B - acustic alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 18 | 31 | DO |  |  | C | 12.1.4 | LP1100B filling dolomia SL1100B - acustic alarm |  | LP1100B | A19 | LP | 21100 | B | _ | 12 | LAHH | A19LP21100B_LAHH | ok | [5 empty] | 0
ID-S01AP1030-00271 | 271 |  | A19LP11150_LI | loc.pan. LP1150 filling dolomia SL1100 - Level indicator |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LP1150 filling dolomia SL1100 - Level indicator |  | LP1150 | A19 | LP | 11150 |  | _ | 11 | LI | A19LP11150_LI | ok | [5 empty] | %
ID-S01AP1030-00272 | 272 |  | A19CD1300A_YLRE | aut.pan. AP1300A cleaning dolomia FF1100A - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.3.1 | 2 | 29 | DI |  |  | C | 12.1.3 | AP1300A cleaning dolomia FF1100A - in remote |  | AP1300A | A19 | CD | 1300 | A | _ | 11 | YLRE | A19CD1300A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00273 | 273 |  | A19CD1300A_YSA | aut.pan. AP1300A cleaning dolomia FF1100A - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.3.1 | 3 | 29 | DI |  |  | C | 12.1.3 | AP1300A cleaning dolomia FF1100A - com.alarm |  | AP1300A | A19 | CD | 1300 | A | _ | 11 | YSA | A19CD1300A_YSA | ok | [5 empty] | 0
ID-S01AP1030-00274 | 274 |  | A19CD1300A_HSH | aut.pan. AP1300A cleaning dolomia FF1100A - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 12 |  | 12.1.4.5 | 19 | 31 | DO |  |  | C | 12.1.4 | AP1300A cleaning dolomia FF1100A - enable |  | AP1300A | A19 | CD | 1300 | A | _ | 11 | HSH | A19CD1300A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00275 | 275 |  | A19CD1300B_YLRE | aut.pan. AP1300B cleaning dolomia FF1100B - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.4.8 | 9 | 26 | DI |  |  | C | 12.1.4 | AP1300B cleaning dolomia FF1100B - in remote |  | AP1300B | A19 | CD | 1300 | B | _ | 11 | YLRE | A19CD1300B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00276 | 276 |  | A19CD1300B_YSA | aut.pan. AP1300B cleaning dolomia FF1100B - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.4.8 | 10 | 26 | DI |  |  | C | 12.1.4 | AP1300B cleaning dolomia FF1100B - com.alarm |  | AP1300B | A19 | CD | 1300 | B | _ | 11 | YSA | A19CD1300B_YSA | ok | [5 empty] | 0
ID-S01AP1030-00277 | 277 |  | A19CD1300B_HSH | aut.pan. AP1300B cleaning dolomia FF1100B - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 12 |  | 12.1.4.5 | 20 | 31 | DO |  |  | C | 12.1.4 | AP1300B cleaning dolomia FF1100B - enable |  | AP1300B | A19 | CD | 1300 | B | _ | 11 | HSH | A19CD1300B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00278 | 278 |  | A19YLRE1358 | aut.pan. AP1358 cleaning dolomia FF1158 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | AP1358 cleaning dolomia FF1158 - in remote |  | AP1358 | A19 | YLRE | 1358 |  |  |  |  | A19YLRE1358 | ok | [5 empty] | 0
ID-S01AP1030-00279 | 279 |  | A19YSA1358 | aut.pan. AP1358 cleaning dolomia FF1158 - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | AP1358 cleaning dolomia FF1158 - com.alarm |  | AP1358 | A19 | YSA | 1358 |  |  |  |  | A19YSA1358 | ok | [5 empty] | 0
ID-S01AP1030-00280 | 280 |  | A19HSH1358 | aut.pan. AP1358 cleaning dolomia FF1158 - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | AP1358 cleaning dolomia FF1158 - enable |  | AP1358 | A19 | HSH | 1358 |  |  |  |  | A19HSH1358 | ok | [5 empty] | 0
ID-S01AP1030-00281 | 281 |  | A19LSH1101A | lev. H LSH1101 dolomia hopper HP1101A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | A | 12.1.7.1 | 16 | 18 | DI |  |  | D | 12.1.7 | H LSH1101 dolomia hopper HP1101A |  | H | A19 | LSH | 1101 | A |  |  |  | A19LSH1101A | ok | [5 empty] | 0
ID-S01AP1030-00282 | 282 |  | A19LSH1101B | lev. H LSH1151 dolomia hopper HP1101B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 15 | 24 | DI |  |  | D | 12.1.6 | H LSH1151 dolomia hopper HP1101B |  | H | A19 | LSH | 1101 | B |  |  |  | A19LSH1101B | ok | [5 empty] | 0
ID-S01AP1030-00283 | 283 |  | A19LSH1158 | lev. H LSH1158 dolomia FF1158 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-004 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | H LSH1158 dolomia FF1158 |  | H | A19 | LSH | 1158 |  |  |  |  | A19LSH1158 | ok | [5 empty] | 0
ID-S01AP1030-00284 | 284 |  | A19LSHH1100A | lev. HH LSHH1100A dolomia silos SL1100A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | A | 12.1.7.1 | 17 | 18 | DI |  |  | D | 12.1.7 | HH LSHH1100A dolomia silos SL1100A |  | HH | A19 | LSHH | 1100 | A |  |  |  | A19LSHH1100A | ok | [5 empty] | 0
ID-S01AP1030-00285 | 285 |  | A19LSHH1100B | lev. HH LSHH1100B dolomia silos SL1100B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 16 | 24 | DI |  |  | D | 12.1.6 | HH LSHH1100B dolomia silos SL1100B |  | HH | A19 | LSHH | 1100 | B |  |  |  | A19LSHH1100B | ok | [5 empty] | 0
ID-S01AP1030-00286 | 286 |  | A19LSL1101A | lev. L LSL1101A dolomia hopper HP1101A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | A | 12.1.7.1 | 18 | 18 | DI |  |  | D | 12.1.7 | L LSL1101A dolomia hopper HP1101A |  | L | A19 | LSL | 1101 | A |  |  |  | A19LSL1101A | ok | [5 empty] | 0
ID-S01AP1030-00287 | 287 |  | A19LSL1101B | lev. L LSL1101B dolomia hopper HP1101B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | B | 12.1.8.7 | 1 | 28 | DI |  |  | D | 12.1.8 | L LSL1101B dolomia hopper HP1101B |  | L | A19 | LSL | 1101 | B |  |  |  | A19LSL1101B | ok | [5 empty] | 0
ID-S01AP1030-00288 | 288 |  | A19LSLL1100A | lev. LL LSLL1100A dolomia silos SL1100A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | A | 12.1.7.2 | 1 | 19 | DI |  |  | D | 12.1.7 | LL LSLL1100A dolomia silos SL1100A |  | LL | A19 | LSLL | 1100 | A |  |  |  | A19LSLL1100A | ok | [5 empty] | 0
ID-S01AP1030-00289 | 289 |  | A19LSLL1100B | lev. LL LSLL1100B dolomia silos SL1100B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 | B | 12.1.8.7 | 2 | 28 | DI |  |  | D | 12.1.8 | LL LSLL1100B dolomia silos SL1100B |  | LL | A19 | LSLL | 1100 | B |  |  |  | A19LSLL1100B | ok | [5 empty] | 0
ID-S01AP1030-00290 | 290 |  | A19LI1100 | lev. LT1100 dolomia silos SL1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LT1100 dolomia silos SL1100 |  | LT1100 | A19 | LI | 1100 |  |  |  |  | A19LI1100 | ok | [5 empty] | %
ID-S01AP1030-00291 | 291 |  | A19LI1150 | lev. LT1150 dolomia silos SL1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LT1150 dolomia silos SL1150 |  | LT1150 | A19 | LI | 1150 |  |  |  |  | A19LI1150 | ok | [5 empty] | %
ID-S01AP1030-00292 | 292 |  | A19POV1102A_ZSH | vlv. POV1102A extract. dolomia silos SL1100A - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.7.2 | 2 | 19 | DI |  |  | C | 12.1.7 | POV1102A extract. dolomia silos SL1100A - opened |  | POV1102A | A19 | POV | 1102 | A | _ | 12 | ZSH | A19POV1102A_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00293 | 293 |  | A19POV1102A_HSH | vlv. POV1102A extract. dolomia silos SL1100A - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 12 | 30 | DO |  |  | C | 12.1.6 | POV1102A extract. dolomia silos SL1100A - open |  | POV1102A | A19 | POV | 1102 | A | _ | 12 | HSH | A19POV1102A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00294 | 294 |  | A19POV1102A_HSL | vlv. POV1102A extract. dolomia silos SL1100A - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 13 | 30 | DO |  |  | C | 12.1.6 | POV1102A extract. dolomia silos SL1100A - close |  | POV1102A | A19 | POV | 1102 | A | _ | 12 | HSL | A19POV1102A_HSL | ok | [5 empty] | 0
ID-S01AP1030-00295 | 295 |  | A19POV1102B_ZSH | vlv. POV1102B extract. dolomia silos SL1100B - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.8.7 | 3 | 28 | DI |  |  | C | 12.1.8 | POV1102B extract. dolomia silos SL1100B - opened |  | POV1102B | A19 | POV | 1102 | B | _ | 12 | ZSH | A19POV1102B_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00296 | 296 |  | A19POV1102B_HSH | vlv. POV1102B extract. dolomia silos SL1100B - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 14 | 30 | DO |  |  | C | 12.1.6 | POV1102B extract. dolomia silos SL1100B - open |  | POV1102B | A19 | POV | 1102 | B | _ | 12 | HSH | A19POV1102B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00297 | 297 |  | A19POV1102B_HSL | vlv. POV1102B extract. dolomia silos SL1100B - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 15 | 30 | DO |  |  | C | 12.1.6 | POV1102B extract. dolomia silos SL1100B - close |  | POV1102B | A19 | POV | 1102 | B | _ | 12 | HSL | A19POV1102B_HSL | ok | [5 empty] | 0
ID-S01AP1030-00298 | 298 |  | A19POV1158_ZSH | vlv. POV1158 dolomia to rotary kiln - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 |  |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | POV1158 dolomia to rotary kiln - opened |  | POV1158 | A19 | POV | 1158 |  | _ | 11 | ZSH | A19POV1158_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00299 | 299 |  | A19POV1158_HSH | vlv. POV1158 dolomia to rotary kiln - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 |  |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | POV1158 dolomia to rotary kiln - open |  | POV1158 | A19 | POV | 1158 |  | _ | 11 | HSH | A19POV1158_HSH | ok | [5 empty] | 0
ID-S01AP1030-00300 | 300 |  | A19POV1158_HSL | vlv. POV1158 dolomia to rotary kiln - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 |  |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | POV1158 dolomia to rotary kiln - close |  | POV1158 | A19 | POV | 1158 |  | _ | 11 | HSL | A19POV1158_HSL | ok | [5 empty] | 0
ID-S01AP1030-00301 | 301 |  | A19PSHH1100A | pres. HH PSHH1100 dolomia compr.air FF1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.7.2 | 3 | 19 | DI |  |  | C | 12.1.7 | HH PSHH1100 dolomia compr.air FF1100 |  | HH | A19 | PSHH | 1100 | A |  |  |  | A19PSHH1100A | ok | [5 empty] | 0
ID-S01AP1030-00302 | 302 |  | A19PSHH1100B | pres. HH PSHH1150 dolomia compr.air FF1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.8.7 | 4 | 28 | DI |  |  | C | 12.1.8 | HH PSHH1150 dolomia compr.air FF1150 |  | HH | A19 | PSHH | 1100 | B |  |  |  | A19PSHH1100B | ok | [5 empty] | 0
ID-S01AP1030-00303 | 303 |  | A19PSHH1158 | pres. HH PSHH1158 dolomia compr.air FF1158 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-004 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | HH PSHH1158 dolomia compr.air FF1158 |  | HH | A19 | PSHH | 1158 |  |  |  |  | A19PSHH1158 | ok | [5 empty] | 0
ID-S01AP1030-00304 | 304 |  | A19PSL1301A | pres. L PSL1301 dolomia compr.air PRV1301 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.7.2 | 4 | 19 | DI |  |  | C | 12.1.7 | L PSL1301 dolomia compr.air PRV1301 |  | L | A19 | PSL | 1301 | A |  |  |  | A19PSL1301A | ok | [5 empty] | 0
ID-S01AP1030-00305 | 305 |  | A19PSL1301B | pres. L PSL1351 dolomia compr.air PRV1351 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.8.7 | 5 | 28 | DI |  |  | C | 12.1.8 | L PSL1351 dolomia compr.air PRV1351 |  | L | A19 | PSL | 1301 | B |  |  |  | A19PSL1301B | ok | [5 empty] | 0
ID-S01AP1030-00306 | 306 |  | A19PSL1358 | pres. L PSL1358 dolomia compr.air PRV1358 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-004 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | L PSL1358 dolomia compr.air PRV1358 |  | L | A19 | PSL | 1358 |  |  |  |  | A19PSL1358 | ok | [5 empty] | 0
ID-S01AP1030-00307 | 307 |  | A19AI1106A | anal. AT1106A dolomia pneu.convey. Dew Point |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | -50 | ¸ | +50 | °C |  | 12 |  | 12.1.5.6 | 4 | 11 | AI |  |  | C | 12.1.5 | AT1106A dolomia pneu.convey. Dew Point |  | AT1106A | A19 | AI | 1106 | A |  |  |  | A19AI1106A | ok |  |  |  | -50 | +50 | °C
ID-S01AP1030-00308 | 308 |  | A19AI1106B | anal. AT1106b dolomia pneu.convey. Dew Point |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | -50 | ¸ | +50 | °C |  | 12 |  | 12.1.5.6 | 5 | 11 | AI |  |  | C | 12.1.5 | AT1106b dolomia pneu.convey. Dew Point |  | AT1106b | A19 | AI | 1106 | B |  |  |  | A19AI1106B | ok |  |  |  | -50 | +50 | °C
ID-S01AP1030-00309 | 309 |  | A19PI1106A | press. PT1106A dolomia pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 4000 | mmH20 |  | 12 |  | 12.1.5.6 | 6 | 11 | AI |  |  | C | 12.1.5 | PT1106A dolomia pneu.convey. |  | PT1106A | A19 | PI | 1106 | A |  |  |  | A19PI1106A | ok |  |  |  | 0 | 4000 | mmH20
ID-S01AP1030-00310 | 310 |  | A19PI1106B | press. PT1106B dolomia pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 4000 | mmH20 |  | 12 |  | 12.1.5.6 | 7 | 11 | AI |  |  | C | 12.1.5 | PT1106B dolomia pneu.convey. |  | PT1106B | A19 | PI | 1106 | B |  |  |  | A19PI1106B | ok |  |  |  | 0 | 4000 | mmH20
ID-S01AP1030-00311 | 311 |  | A19RV1107A_YLRE | rot.vlv. RV1107A dolomia pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 16 | 30 | DI |  |  | C | 12.1.1 | RV1107A dolomia pneu.convey. - in remote |  | RV1107A | A19 | RV | 1107 | A | _ | 11 | YLRE | A19RV1107A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00312 | 312 |  | A19RV1107A_YLH | rot.vlv. RV1107A dolomia pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 17 | 30 | DI |  |  | C | 12.1.1 | RV1107A dolomia pneu.convey. - in running |  | RV1107A | A19 | RV | 1107 | A | _ | 11 | YLH | A19RV1107A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00313 | 313 |  | A19RV1107A_YSG | rot.vlv. RV1107A dolomia pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 18 | 30 | DI |  |  | C | 12.1.1 | RV1107A dolomia pneu.convey. - supply fault |  | RV1107A | A19 | RV | 1107 | A | _ | 11 | YSG | A19RV1107A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00314 | 314 |  | A19RV1107A_HSH | rot.vlv. RV1107A dolomia pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 22 | 39 | DO |  |  | C | 12.1.2 | RV1107A dolomia pneu.convey. - start/stop |  | RV1107A | A19 | RV | 1107 | A | _ | 11 | HSH | A19RV1107A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00315 | 315 |  | A19RV1107B_YLRE | rot.vlv. RV1107B dolomia pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 19 | 30 | DI |  |  | C | 12.1.2 | RV1107B dolomia pneu.convey. - in remote |  | RV1107B | A19 | RV | 1107 | B | _ | 11 | YLRE | A19RV1107B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00316 | 316 |  | A19RV1107B_YLH | rot.vlv. RV1107B dolomia pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 20 | 30 | DI |  |  | C | 12.1.2 | RV1107B dolomia pneu.convey. - in running |  | RV1107B | A19 | RV | 1107 | B | _ | 11 | YLH | A19RV1107B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00317 | 317 |  | A19RV1107B_YSG | rot.vlv. RV1107B dolomia pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 21 | 30 | DI |  |  | C | 12.1.2 | RV1107B dolomia pneu.convey. - supply fault |  | RV1107B | A19 | RV | 1107 | B | _ | 11 | YSG | A19RV1107B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00318 | 318 |  | A19RV1107B_HSH | rot.vlv. RV1107B dolomia pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 23 | 39 | DO |  |  | C | 12.1.2 | RV1107B dolomia pneu.convey. - start/stop |  | RV1107B | A19 | RV | 1107 | B | _ | 11 | HSH | A19RV1107B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00319 | 319 |  | A19RV1159_YLRE | rot.vlv. RV1159 dolomia pneu.convey. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | RV1159 dolomia pneu.convey. - in remote |  | RV1159 | A19 | RV | 1159 |  | _ | 10 | YLRE | A19RV1159_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00320 | 320 |  | A19RV1159_YLH | rot.vlv. RV1159 dolomia pneu.convey. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | RV1159 dolomia pneu.convey. - in running |  | RV1159 | A19 | RV | 1159 |  | _ | 10 | YLH | A19RV1159_YLH | ok | [5 empty] | 0
ID-S01AP1030-00321 | 321 |  | A19RV1159_YSG | rot.vlv. RV1159 dolomia pneu.convey. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | RV1159 dolomia pneu.convey. - supply fault |  | RV1159 | A19 | RV | 1159 |  | _ | 10 | YSG | A19RV1159_YSG | ok | [5 empty] | 0
ID-S01AP1030-00322 | 322 |  | A19RV1159_HSH | rot.vlv. RV1159 dolomia pneu.convey. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | RV1159 dolomia pneu.convey. - start/stop |  | RV1159 | A19 | RV | 1159 |  | _ | 10 | HSH | A19RV1159_HSH | ok | [5 empty] | 0
ID-S01AP1030-00323 | 323 |  | A19SOV1304A_HSH | vlv. SOV1304A fluid dolomia compr.air SI1100A - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 16 | 30 | DO |  |  | C | 12.1.6 | SOV1304A fluid dolomia compr.air SI1100A - open |  | SOV1304A | A19 | SOV | 1304 | A | _ | 12 | HSH | A19SOV1304A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00324 | 324 |  | A19SOV1305A_HSH | vlv. SOV1305A fluid dolomia compr.air SI1100A - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 17 | 30 | DO |  |  | C | 12.1.6 | SOV1305A fluid dolomia compr.air SI1100A - open |  | SOV1305A | A19 | SOV | 1305 | A | _ | 12 | HSH | A19SOV1305A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00325 | 325 |  | A19SOV1306A_HSH | vlv. SOV1306A fluid dolomia compr.air HP1101A - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 18 | 30 | DO |  |  | C | 12.1.6 | SOV1306A fluid dolomia compr.air HP1101A - open |  | SOV1306A | A19 | SOV | 1306 | A | _ | 12 | HSH | A19SOV1306A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00326 | 326 |  | A19TI1106A | temp. TT1106A dolomia pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | °C |  | 12 |  | 12.1.5.6 | 8 | 11 | AI |  |  | C | 12.1.5 | TT1106A dolomia pneu.convey. |  | TT1106A | A19 | TI | 1106 | A |  |  |  | A19TI1106A | ok |  |  |  | 0 | 100 | °C
ID-S01AP1030-00327 | 327 |  | A19TI1106B | temp. TT1106b dolomia pneu.convey. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | °C |  | 12 |  | 12.1.5.6 | 9 | 11 | AI |  |  | C | 12.1.5 | TT1106b dolomia pneu.convey. |  | TT1106b | A19 | TI | 1106 | B |  |  |  | A19TI1106B | ok |  |  |  | 0 | 100 | °C
ID-S01AP1030-00328 | 328 |  | A19SOV1304B_HSH | vlv. SOV1304B fluid dolomia compr.air SI1100B - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 19 | 30 | DO |  |  | C | 12.1.6 | SOV1304B fluid dolomia compr.air SI1100B - open |  | SOV1304B | A19 | SOV | 1304 | B | _ | 12 | HSH | A19SOV1304B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00329 | 329 |  | A19SOV1305B_HSH | vlv. SOV1305B fluid dolomia compr.air SI1100B - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 20 | 30 | DO |  |  | C | 12.1.6 | SOV1305B fluid dolomia compr.air SI1100B - open |  | SOV1305B | A19 | SOV | 1305 | B | _ | 12 | HSH | A19SOV1305B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00330 | 330 |  | A19SOV1356B_HSH | vlv. SOV1306B fluid dolomia compr.air HP1100B - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 21 | 30 | DO |  |  | C | 12.1.6 | SOV1306B fluid dolomia compr.air HP1100B - open |  | SOV1306B | A19 | SOV | 1356 | B | _ | 12 | HSH | A19SOV1356B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00331 | 331 |  | A19SOV1357_HSH | vlv. SOV1357 fluid dolomia EL1156 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 |  |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | SOV1357 fluid dolomia EL1156 - open |  | SOV1357 | A19 | SOV | 1357 |  | _ | 11 | HSH | A19SOV1357_HSH | ok | [5 empty] | 0
ID-S01AP1030-00332 | 332 |  | A19SSL1103A | speed L SSL1103 dolomia conveyor SW1103A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 19 | 30 | DI |  |  | C | 12.1.1 | L SSL1103 dolomia conveyor SW1103A |  | L | A19 | SSL | 1103 | A |  |  |  | A19SSL1103A | ok | [5 empty] | 0
ID-S01AP1030-00333 | 333 |  | A19SSL1104A | speed L SSL1104 dolomia conveyor SW1104A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 20 | 30 | DI |  |  | C | 12.1.1 | L SSL1104 dolomia conveyor SW1104A |  | L | A19 | SSL | 1104 | A |  |  |  | A19SSL1104A | ok | [5 empty] | 0
ID-S01AP1030-00334 | 334 |  | A19SSL1107A | speed L SSL1107 dolomia rot.vlv. RV1107A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 21 | 30 | DI |  |  | C | 12.1.1 | L SSL1107 dolomia rot.vlv. RV1107A |  | L | A19 | SSL | 1107 | A |  |  |  | A19SSL1107A | ok | [5 empty] | 0
ID-S01AP1030-00335 | 335 |  | A19SSL1103B | speed L SSL1153 dolomia conveyor SW1103B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.8.7 | 6 | 28 | DI |  |  | C | 12.1.8 | L SSL1153 dolomia conveyor SW1103B |  | L | A19 | SSL | 1103 | B |  |  |  | A19SSL1103B | ok | [5 empty] | 0
ID-S01AP1030-00336 | 336 |  | A19SSL1104B | speed L SSL1104B dolomia conveyor SW1104B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.8.7 | 7 | 28 | DI |  |  | C | 12.1.8 | L SSL1104B dolomia conveyor SW1104B |  | L | A19 | SSL | 1104 | B |  |  |  | A19SSL1104B | ok | [5 empty] | 0
ID-S01AP1030-00337 | 337 |  | A19SSL1107B | speed L SSL1157 dolomia rot.vlv. RV1107B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.8.7 | 8 | 28 | DI |  |  | C | 12.1.8 | L SSL1157 dolomia rot.vlv. RV1107B |  | L | A19 | SSL | 1107 | B |  |  |  | A19SSL1107B | ok | [5 empty] | 0
ID-S01AP1030-00338 | 338 |  | A19SSL1159 | speed L SSL1159 dolomia rot.vlv. RV1159 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-004 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | L SSL1159 dolomia rot.vlv. RV1159 |  | L | A19 | SSL | 1159 |  |  |  |  | A19SSL1159 | ok | [5 empty] | 0
ID-S01AP1030-00339 | 339 |  | A19SW1103A_YLRE | screw conv. SW1103A extract. dolomia - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 22 | 30 | DI |  |  | C | 12.1.1 | conv. SW1103A extract. dolomia - in remote |  | conv. | A19 | SW | 1103 | A | _ | 11 | YLRE | A19SW1103A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00340 | 340 |  | A19SW1103A_YLH | screw conv. SW1103A extract. dolomia - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 23 | 30 | DI |  |  | C | 12.1.1 | conv. SW1103A extract. dolomia - in running |  | conv. | A19 | SW | 1103 | A | _ | 11 | YLH | A19SW1103A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00341 | 341 |  | A19SW1103A_YSG | screw conv. SW1103A extract. dolomia - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 24 | 30 | DI |  |  | C | 12.1.1 | conv. SW1103A extract. dolomia - supply fault |  | conv. | A19 | SW | 1103 | A | _ | 11 | YSG | A19SW1103A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00342 | 342 |  | A19SW1103A_HSH | screw conv. SW1103A extract. dolomia - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 24 | 39 | DO |  |  | C | 12.1.2 | conv. SW1103A extract. dolomia - start/stop |  | conv. | A19 | SW | 1103 | A | _ | 11 | HSH | A19SW1103A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00343 | 343 |  | A19SW1104A_YLRE | screw conv. SW1104A dosag. dolomia - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 25 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. dolomia - in remote |  | conv. | A19 | SW | 1104 | A | _ | 11 | YLRE | A19SW1104A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00344 | 344 |  | A19SW1104A_YLH | screw conv. SW1104A dosag. dolomia - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.1.2 | 26 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. dolomia - in running |  | conv. | A19 | SW | 1104 | A | _ | 11 | YLH | A19SW1104A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00345 | 345 |  | A19SW1104A_YS | screw conv. SW1104A dosag. dolomia - gen.fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 27 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. dolomia - gen.fault |  | conv. | A19 | SW | 1104 | A | _ | 11 | YS | A19SW1104A_YS | ok | [5 empty] | 0
ID-S01AP1030-00346 | 346 |  | A19SW1104A_YSG | screw conv. SW1104A dosag. dolomia - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.1.2 | 28 | 30 | DI |  |  | C | 12.1.1 | conv. SW1104A dosag. dolomia - supply fault |  | conv. | A19 | SW | 1104 | A | _ | 11 | YSG | A19SW1104A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00347 | 347 |  | A19SW1104A_HSH | screw conv. SW1104A dosag. dolomia - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 25 | 39 | DO |  |  | C | 12.1.2 | conv. SW1104A dosag. dolomia - start/stop |  | conv. | A19 | SW | 1104 | A | _ | 11 | HSH | A19SW1104A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00348 | 348 |  | A19SW1104A_SI | screw conv. SW1104A dosag. dolomia - speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.7 | 9 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104A dosag. dolomia - speed |  | conv. | A19 | SW | 1104 | A | _ | 11 | SI | A19SW1104A_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00349 | 349 |  | A19SW1104A_II | screw conv. SW1104A dosag. dolomia - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 12 |  | 12.1.1.7 | 10 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104A dosag. dolomia - current |  | conv. | A19 | SW | 1104 | A | _ | 11 | II | A19SW1104A_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1030-00350 | 350 |  | A19SW1104A_SY | screw conv. SW1104A dosag. dolomia - req.speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.8 | 5 | 8 | AO |  |  | C | 12.1.1 | conv. SW1104A dosag. dolomia - req.speed |  | conv. | A19 | SW | 1104 | A | _ | 11 | SY | A19SW1104A_SY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00351 | 351 |  | A19SW1103B_YLRE | screw conv. SW1103B extract. dolomia - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 22 | 30 | DI |  |  | C | 12.1.2 | conv. SW1103B extract. dolomia - in remote |  | conv. | A19 | SW | 1103 | B | _ | 11 | YLRE | A19SW1103B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00352 | 352 |  | A19SW1103B_YLH | screw conv. SW1103B extract. dolomia - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 23 | 30 | DI |  |  | C | 12.1.2 | conv. SW1103B extract. dolomia - in running |  | conv. | A19 | SW | 1103 | B | _ | 11 | YLH | A19SW1103B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00353 | 353 |  | A19SW1103B_YSG | screw conv. SW1103B extract. dolomia - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 24 | 30 | DI |  |  | C | 12.1.2 | conv. SW1103B extract. dolomia - supply fault |  | conv. | A19 | SW | 1103 | B | _ | 11 | YSG | A19SW1103B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00354 | 354 |  | A19SW1103B_HSH | screw conv. SW1103B extract. dolomia - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 26 | 39 | DO |  |  | C | 12.1.2 | conv. SW1103B extract. dolomia - start/stop |  | conv. | A19 | SW | 1103 | B | _ | 11 | HSH | A19SW1103B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00355 | 355 |  | A19SW1104B_YLRE | screw conv. SW1104B dosag. dolomia - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 25 | 30 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. dolomia - in remote |  | conv. | A19 | SW | 1104 | B | _ | 11 | YLRE | A19SW1104B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00356 | 356 |  | A19SW1104B_YLH | screw conv. SW1104B dosag. dolomia - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.2.7 | 26 | 30 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. dolomia - in running |  | conv. | A19 | SW | 1104 | B | _ | 11 | YLH | A19SW1104B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00357 | 357 |  | A19SW1104B_YS | screw conv. SW1104B dosag. dolomia - gen.fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 27 | 30 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. dolomia - gen.fault |  | conv. | A19 | SW | 1104 | B | _ | 11 | YS | A19SW1104B_YS | ok | [5 empty] | 0
ID-S01AP1030-00358 | 358 |  | A19SW1104B_YSG | screw conv. SW1104B dosag. dolomia - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.2.7 | 28 | 30 | DI |  |  | C | 12.1.2 | conv. SW1104B dosag. dolomia - supply fault |  | conv. | A19 | SW | 1104 | B | _ | 11 | YSG | A19SW1104B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00359 | 359 |  | A19SW1104B_HSH | screw conv. SW1104B dosag. dolomia - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 27 | 39 | DO |  |  | C | 12.1.2 | conv. SW1104B dosag. dolomia - start/stop |  | conv. | A19 | SW | 1104 | B | _ | 11 | HSH | A19SW1104B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00360 | 360 |  | A19SW1104B_SI | screw conv. SW1104B dosag. dolomia - speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.7 | 11 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104B dosag. dolomia - speed |  | conv. | A19 | SW | 1104 | B | _ | 11 | SI | A19SW1104B_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00361 | 361 |  | A19SW1104B_II | screw conv. SW1104B dosag. dolomia - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 12 |  | 12.1.1.7 | 12 | 14 | AI |  |  | H | 12.1.1 | conv. SW1104B dosag. dolomia - current |  | conv. | A19 | SW | 1104 | B | _ | 11 | II | A19SW1104B_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1030-00362 | 362 |  | A19SW1104B_SY | screw conv. SW1104B dosag. dolomia - req.speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.8 | 6 | 8 | AO |  |  | C | 12.1.1 | conv. SW1104B dosag. dolomia - req.speed |  | conv. | A19 | SW | 1104 | B | _ | 11 | SY | A19SW1104B_SY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00363 | 363 |  | A19WI1100A | weight WT1100A dolomia silos SL1100A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 100 | ton | 220 Vac / .. | 12 |  | 12.1.5.6 | 10 | 11 | AI |  |  | H | 12.1.5 | WT1100A dolomia silos SL1100A |  | WT1100A | A19 | WI | 1100 | A |  |  |  | A19WI1100A | ok |  |  |  | 0 | 100 | ton
ID-S01AP1030-00364 | 364 |  | A19WI1100B | weight WT1100B dolomia silos SL1100B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 100 | ton | 220 Vac / .. | 12 |  | 12.1.5.6 | 11 | 11 | AI |  |  | H | 12.1.5 | WT1100B dolomia silos SL1100B |  | WT1100B | A19 | WI | 1100 | B |  |  |  | A19WI1100B | ok |  |  |  | 0 | 100 | ton
ID-S01AP1030-00365 | 365 |  | A19ZSH1100A | pos. H ZSH1100A filling dolomia SL1100A |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.7.2 | 5 | 19 | DI |  |  | C | 12.1.7 | H ZSH1100A filling dolomia SL1100A |  | H | A19 | ZSH | 1100 | A |  |  |  | A19ZSH1100A | ok | [5 empty] | 0
ID-S01AP1030-00366 | 366 |  | A19ZSH1100B | pos. H ZSH1100B filling dolomia SL1100B |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | CHN1-TDZ2-A19-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.8.7 | 9 | 28 | DI |  |  | C | 12.1.8 | H ZSH1100B filling dolomia SL1100B |  | H | A19 | ZSH | 1100 | B |  |  |  | A19ZSH1100B | ok | [5 empty] | 0
ID-S01AP1030-00367 | 367 |  | A19DR1108A_YLH | dryer DR1108A dolomia pneu.convey.- in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | in marcia | 0 |  | 12 | A | 12.1.1.2 | 29 | 30 | DI |  |  | C | 12.1.1 | DR1108A dolomia pneu.convey.- in running |  | DR1108A | A19 | DR | 1108 | A | _ | 11 | YLH | A19DR1108A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00368 | 368 |  | A19DR1108A_YSA | dryer DR1108A dolomia pneu.convey.- com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | allarme | 0 |  | 12 | A | 12.1.1.2 | 30 | 30 | DI |  |  | C | 12.1.1 | DR1108A dolomia pneu.convey.- com.alarm |  | DR1108A | A19 | DR | 1108 | A | _ | 11 | YSA | A19DR1108A_YSA | ok | [5 empty] | 0
ID-S01AP1030-00369 | 369 |  | A19DR1108A_HSH | dryer DR1108A dolomia pneu.convey.- start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 28 | 39 | DO |  |  | C | 12.1.2 | DR1108A dolomia pneu.convey.- start/stop |  | DR1108A | A19 | DR | 1108 | A | _ | 11 | HSH | A19DR1108A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00370 | 370 |  | A19DR1108B_YLH | dryer DR1108B dolomia pneu.convey.- in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | in marcia | 0 |  | 12 | B | 12.1.2.7 | 29 | 30 | DI |  |  | C | 12.1.2 | DR1108B dolomia pneu.convey.- in running |  | DR1108B | A19 | DR | 1108 | B | _ | 11 | YLH | A19DR1108B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00371 | 371 |  | A19DR1108B_YSA | dryer DR1108B dolomia pneu.convey.- com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | allarme | 0 |  | 12 | B | 12.1.2.7 | 30 | 30 | DI |  |  | C | 12.1.2 | DR1108B dolomia pneu.convey.- com.alarm |  | DR1108B | A19 | DR | 1108 | B | _ | 11 | YSA | A19DR1108B_YSA | ok | [5 empty] | 0
ID-S01AP1030-00372 | 372 |  | A19DR1108B_HSH | dryer DR1108B dolomia pneu.convey.- start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 A19 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 29 | 39 | DO |  |  | C | 12.1.2 | DR1108B dolomia pneu.convey.- start/stop |  | DR1108B | A19 | DR | 1108 | B | _ | 11 | HSH | A19DR1108B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00373 | 373 |  | P30CK1300A_YLH | compr. CK1300A FG quenc. compr.air - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | in marcia | 0 |  | 12 | A | 12.1.5.1 | 1 | 28 | DI |  |  | C | 12.1.5 | CK1300A FG quenc. compr.air - in running |  | CK1300A | P30 | CK | 1300 | A | _ | 11 | YLH | P30CK1300A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00374 | 374 |  | P30CK1300A_YSA | compr. CK1300A FG quenc. compr.air - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | allarme | 0 |  | 12 | A | 12.1.5.1 | 2 | 28 | DI |  |  | C | 12.1.5 | CK1300A FG quenc. compr.air - com.alarm |  | CK1300A | P30 | CK | 1300 | A | _ | 11 | YSA | P30CK1300A_YSA | ok | [5 empty] | 0
ID-S01AP1030-00375 | 375 |  | P30CK1300A_HSH | compr. CK1300A FG quenc. compr.air - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | abilitaz. | 0 |  | 12 |  | 12.1.5.4 | 1 | 31 | DO |  |  | C | 12.1.5 | CK1300A FG quenc. compr.air - enable |  | CK1300A | P30 | CK | 1300 | A | _ | 11 | HSH | P30CK1300A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00376 | 376 |  | P30CK1300B_YLH | compr. CK1300B FG quenc. compr.air - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | in marcia | 0 |  | 12 | B | 12.1.6.6 | 17 | 24 | DI |  |  | C | 12.1.6 | CK1300B FG quenc. compr.air - in running |  | CK1300B | P30 | CK | 1300 | B | _ | 11 | YLH | P30CK1300B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00377 | 377 |  | P30CK1300B_YSA | compr. CK1300B FG quenc. compr.air - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | allarme | 0 |  | 12 | B | 12.1.6.6 | 18 | 24 | DI |  |  | C | 12.1.6 | CK1300B FG quenc. compr.air - com.alarm |  | CK1300B | P30 | CK | 1300 | B | _ | 11 | YSA | P30CK1300B_YSA | ok | [5 empty] | 0
ID-S01AP1030-00378 | 378 |  | P30CK1300B_HSH | compr. CK1300B FG quenc. compr.air - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | abilitaz. | 0 |  | 12 |  | 12.1.5.4 | 2 | 31 | DO |  |  | C | 12.1.5 | CK1300B FG quenc. compr.air - enable |  | CK1300B | P30 | CK | 1300 | B | _ | 11 | HSH | P30CK1300B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00379 | 379 |  | P30EH1220_YLH | elec.heater EH1220 FG quenc. TK1200 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 3 | 28 | DI |  |  | C | 12.1.5 | EH1220 FG quenc. TK1200 - in running |  | EH1220 | P30 | EH | 1220 |  | _ | 10 | YLH | P30EH1220_YLH | ok | [5 empty] | 0
ID-S01AP1030-00380 | 380 |  | P30EH1220_YSG | elec.heater EH1220 FG quenc. TK1200 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 4 | 28 | DI |  |  | C | 12.1.5 | EH1220 FG quenc. TK1200 - supply fault |  | EH1220 | P30 | EH | 1220 |  | _ | 10 | YSG | P30EH1220_YSG | ok | [5 empty] | 0
ID-S01AP1030-00381 | 381 |  | P30EH1220_HSH | elec.heater EH1220 FG quenc. TK1200 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 3 | 31 | DO |  |  | C | 12.1.5 | EH1220 FG quenc. TK1200 - start/stop |  | EH1220 | P30 | EH | 1220 |  | _ | 10 | HSH | P30EH1220_HSH | ok | [5 empty] | 0
ID-S01AP1030-00382 | 382 |  | P30EH1221_YLH | elec.heater EH1221 FG quenc. recircul - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 5 | 28 | DI |  |  | C | 12.1.5 | EH1221 FG quenc. recircul - in running |  | EH1221 | P30 | EH | 1221 |  | _ | 10 | YLH | P30EH1221_YLH | ok | [5 empty] | 0
ID-S01AP1030-00383 | 383 |  | P30EH1221_YSG | elec.heater EH1221 FG quenc. recircul - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 6 | 28 | DI |  |  | C | 12.1.5 | EH1221 FG quenc. recircul - supply fault |  | EH1221 | P30 | EH | 1221 |  | _ | 10 | YSG | P30EH1221_YSG | ok | [5 empty] | 0
ID-S01AP1030-00384 | 384 |  | P30EH1221_HSH | elec.heater EH1221 FG quenc. recircul - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 4 | 31 | DO |  |  | C | 12.1.5 | EH1221 FG quenc. recircul - start/stop |  | EH1221 | P30 | EH | 1221 |  | _ | 10 | HSH | P30EH1221_HSH | ok | [5 empty] | 0
ID-S01AP1030-00385 | 385 |  | P30EH1222_YLH | elec.heater EH1222 FG quenc. water to nebul 1- in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 7 | 28 | DI |  |  | C | 12.1.5 | EH1222 FG quenc. water to nebul 1- in running |  | EH1222 | P30 | EH | 1222 |  | _ | 10 | YLH | P30EH1222_YLH | ok | [5 empty] | 0
ID-S01AP1030-00386 | 386 |  | P30EH1222_YSG | elec.heater EH1222 FG quenc. water to nebul 1- supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 8 | 28 | DI |  |  | C | 12.1.5 | EH1222 FG quenc. water to nebul 1- supply fault |  | EH1222 | P30 | EH | 1222 |  | _ | 10 | YSG | P30EH1222_YSG | ok | [5 empty] | 0
ID-S01AP1030-00387 | 387 |  | P30EH1222_HSH | elec.heater EH1222 FG quenc. water to nebul 1- start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 5 | 31 | DO |  |  | C | 12.1.5 | EH1222 FG quenc. water to nebul 1- start/stop |  | EH1222 | P30 | EH | 1222 |  | _ | 10 | HSH | P30EH1222_HSH | ok | [5 empty] | 0
ID-S01AP1030-00388 | 388 |  | P30EH1223_YLH | elec.heater EH1223 FG quenc. water to nebul 2- in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 9 | 28 | DI |  |  | C | 12.1.5 | EH1223 FG quenc. water to nebul 2- in running |  | EH1223 | P30 | EH | 1223 |  | _ | 10 | YLH | P30EH1223_YLH | ok | [5 empty] | 0
ID-S01AP1030-00389 | 389 |  | P30EH1223_YSG | elec.heater EH1223 FG quenc. water to nebul 2- supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 10 | 28 | DI |  |  | C | 12.1.5 | EH1223 FG quenc. water to nebul 2- supply fault |  | EH1223 | P30 | EH | 1223 |  | _ | 10 | YSG | P30EH1223_YSG | ok | [5 empty] | 0
ID-S01AP1030-00390 | 390 |  | P30EH1223_HSH | elec.heater EH1223 FG quenc. water to nebul 2- start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 6 | 31 | DO |  |  | C | 12.1.5 | EH1223 FG quenc. water to nebul 2- start/stop |  | EH1223 | P30 | EH | 1223 |  | _ | 10 | HSH | P30EH1223_HSH | ok | [5 empty] | 0
ID-S01AP1030-00391 | 391 |  | P30EH1224_YLH | elec.heater EH1224 FG quenc. water to nebul 3- in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 11 | 28 | DI |  |  | C | 12.1.5 | EH1224 FG quenc. water to nebul 3- in running |  | EH1224 | P30 | EH | 1224 |  | _ | 10 | YLH | P30EH1224_YLH | ok | [5 empty] | 0
ID-S01AP1030-00392 | 392 |  | P30EH1224_YSG | elec.heater EH1224 FG quenc. water to nebul 3- supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 12 | 28 | DI |  |  | C | 12.1.5 | EH1224 FG quenc. water to nebul 3- supply fault |  | EH1224 | P30 | EH | 1224 |  | _ | 10 | YSG | P30EH1224_YSG | ok | [5 empty] | 0
ID-S01AP1030-00393 | 393 |  | P30EH1224_HSH | elec.heater EH1224 FG quenc. water to nebul 3- start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 7 | 31 | DO |  |  | C | 12.1.5 | EH1224 FG quenc. water to nebul 3- start/stop |  | EH1224 | P30 | EH | 1224 |  | _ | 10 | HSH | P30EH1224_HSH | ok | [5 empty] | 0
ID-S01AP1030-00394 | 394 |  | P30EH1320_YLH | elec.heater EH1320 FG quenc. PRV1300 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 13 | 28 | DI |  |  | C | 12.1.5 | EH1320 FG quenc. PRV1300 - in running |  | EH1320 | P30 | EH | 1320 |  | _ | 10 | YLH | P30EH1320_YLH | ok | [5 empty] | 0
ID-S01AP1030-00395 | 395 |  | P30EH1320_YSG | elec.heater EH1320 FG quenc. PRV1300 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 14 | 28 | DI |  |  | C | 12.1.5 | EH1320 FG quenc. PRV1300 - supply fault |  | EH1320 | P30 | EH | 1320 |  | _ | 10 | YSG | P30EH1320_YSG | ok | [5 empty] | 0
ID-S01AP1030-00396 | 396 |  | P30EH1320_HSH | elec.heater EH1320 FG quenc. PRV1300 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 8 | 31 | DO |  |  | C | 12.1.5 | EH1320 FG quenc. PRV1300 - start/stop |  | EH1320 | P30 | EH | 1320 |  | _ | 10 | HSH | P30EH1320_HSH | ok | [5 empty] | 0
ID-S01AP1030-00397 | 397 |  | P30EH1321_YLH | elec.heater EH1321 FG quenc. service air - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 15 | 28 | DI |  |  | C | 12.1.5 | EH1321 FG quenc. service air - in running |  | EH1321 | P30 | EH | 1321 |  | _ | 10 | YLH | P30EH1321_YLH | ok | [5 empty] | 0
ID-S01AP1030-00398 | 398 |  | P30EH1321_YSG | elec.heater EH1321 FG quenc. service air - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 16 | 28 | DI |  |  | C | 12.1.5 | EH1321 FG quenc. service air - supply fault |  | EH1321 | P30 | EH | 1321 |  | _ | 10 | YSG | P30EH1321_YSG | ok | [5 empty] | 0
ID-S01AP1030-00399 | 399 |  | P30EH1321_HSH | elec.heater EH1321 FG quenc. service air - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 9 | 31 | DO |  |  | C | 12.1.5 | EH1321 FG quenc. service air - start/stop |  | EH1321 | P30 | EH | 1321 |  | _ | 10 | HSH | P30EH1321_HSH | ok | [5 empty] | 0
ID-S01AP1030-00400 | 400 |  | P30EH1322_YLH | elec.heater EH1322 FG quenc. service air - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 17 | 28 | DI |  |  | C | 12.1.5 | EH1322 FG quenc. service air - in running |  | EH1322 | P30 | EH | 1322 |  | _ | 10 | YLH | P30EH1322_YLH | ok | [5 empty] | 0
ID-S01AP1030-00401 | 401 |  | P30EH1322_YSG | elec.heater EH1322 FG quenc. service air - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 18 | 28 | DI |  |  | C | 12.1.5 | EH1322 FG quenc. service air - supply fault |  | EH1322 | P30 | EH | 1322 |  | _ | 10 | YSG | P30EH1322_YSG | ok | [5 empty] | 0
ID-S01AP1030-00402 | 402 |  | P30EH1322_HSH | elec.heater EH1322 FG quenc. service air - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 10 | 31 | DO |  |  | C | 12.1.5 | EH1322 FG quenc. service air - start/stop |  | EH1322 | P30 | EH | 1322 |  | _ | 10 | HSH | P30EH1322_HSH | ok | [5 empty] | 0
ID-S01AP1030-00403 | 403 |  | P30FI1201 | flow FT1201 recirc. FG quenc. wat.util. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 80 | m3/h | 220 Vac / .. | 12 |  | 12.1.6.3 | 1 | 15 | AI |  |  | H | 12.1.6 | FT1201 recirc. FG quenc. wat.util. |  | FT1201 | P30 | FI | 1201 |  |  |  |  | P30FI1201 | ok |  |  |  | 0 | 80 | m3/h
ID-S01AP1030-00404 | 404 |  | P30FI1210 | flow FT1210 FG quenc. wat.util. to NZ1110 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 10 | m3/h | 220 Vac / .. | 12 |  | 12.1.6.3 | 2 | 15 | AI |  |  | H | 12.1.6 | FT1210 FG quenc. wat.util. to NZ1110 |  | FT1210 | P30 | FI | 1210 |  |  |  |  | P30FI1210 | ok |  |  |  | 0 | 10 | m3/h
ID-S01AP1030-00405 | 405 |  | P30FI1211 | flow FT1211 FG quenc. wat.util. to NZ1111 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 10 | m3/h | 220 Vac / .. | 12 |  | 12.1.6.3 | 3 | 15 | AI |  |  | H | 12.1.6 | FT1211 FG quenc. wat.util. to NZ1111 |  | FT1211 | P30 | FI | 1211 |  |  |  |  | P30FI1211 | ok |  |  |  | 0 | 10 | m3/h
ID-S01AP1030-00406 | 406 |  | P30FI1212 | flow FT1212 FG quenc. wat.util. to NZ1112 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 10 | m3/h | 220 Vac / .. | 12 |  | 12.1.6.3 | 4 | 15 | AI |  |  | H | 12.1.6 | FT1212 FG quenc. wat.util. to NZ1112 |  | FT1212 | P30 | FI | 1212 |  |  |  |  | P30FI1212 | ok |  |  |  | 0 | 10 | m3/h
ID-S01AP1030-00407 | 407 |  | P30FI1301 | flow FT1301 FG quenc. compr.air to NZ1110 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 1000 | Nm3/h | 220 Vac / .. | 12 |  | 12.1.6.3 | 5 | 15 | AI |  |  | H | 12.1.6 | FT1301 FG quenc. compr.air to NZ1110 |  | FT1301 | P30 | FI | 1301 |  |  |  |  | P30FI1301 | ok |  |  |  | 0 | 1000 | Nm3/h
ID-S01AP1030-00408 | 408 |  | P30FI1302 | flow FT1302 FG quenc. compr.air to NZ1111 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 1000 | Nm3/h | 220 Vac / .. | 12 |  | 12.1.6.3 | 6 | 15 | AI |  |  | H | 12.1.6 | FT1302 FG quenc. compr.air to NZ1111 |  | FT1302 | P30 | FI | 1302 |  |  |  |  | P30FI1302 | ok |  |  |  | 0 | 1000 | Nm3/h
ID-S01AP1030-00409 | 409 |  | P30FI1303 | flow FT1303 FG quenc. compr.air to NZ1112 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 1000 | Nm3/h | 220 Vac / .. | 12 |  | 12.1.6.3 | 7 | 15 | AI |  |  | H | 12.1.6 | FT1303 FG quenc. compr.air to NZ1112 |  | FT1303 | P30 | FI | 1303 |  |  |  |  | P30FI1303 | ok |  |  |  | 0 | 1000 | Nm3/h
ID-S01AP1030-00410 | 410 |  | P30FV1201_ZSL | vlv. FV1201 recirc. FG quenc. wat.util. - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 6 | 19 | DI |  |  | C | 12.1.7 | FV1201 recirc. FG quenc. wat.util. - closed |  | FV1201 | P30 | FV | 1201 |  | _ | 10 | ZSL | P30FV1201_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00411 | 411 |  | P30FV1201_ZY | vlv. FV1201 recirc. FG quenc. wat.util. - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.5.8 | 1 | 6 | AO |  |  | C | 12.1.5 | FV1201 recirc. FG quenc. wat.util. - req.pos. |  | FV1201 | P30 | FV | 1201 |  | _ | 10 | ZY | P30FV1201_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00412 | 412 |  | P30FV1210_ZSL | vlv. FV1210 FG quenc. wat.util. to NZ1110 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 7 | 19 | DI |  |  | C | 12.1.7 | FV1210 FG quenc. wat.util. to NZ1110 - closed |  | FV1210 | P30 | FV | 1210 |  | _ | 10 | ZSL | P30FV1210_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00413 | 413 |  | P30FV1210_ZY | vlv. FV1210 FG quenc. wat.util. to NZ1110 - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.5.8 | 2 | 6 | AO |  |  | C | 12.1.5 | FV1210 FG quenc. wat.util. to NZ1110 - req.pos. |  | FV1210 | P30 | FV | 1210 |  | _ | 10 | ZY | P30FV1210_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00414 | 414 |  | P30FV1211_ZSL | vlv. FV1211 FG quenc. wat.util. to NZ1111 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 8 | 19 | DI |  |  | C | 12.1.7 | FV1211 FG quenc. wat.util. to NZ1111 - closed |  | FV1211 | P30 | FV | 1211 |  | _ | 10 | ZSL | P30FV1211_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00415 | 415 |  | P30FV1211_ZY | vlv. FV1211 FG quenc. wat.util. to NZ1111 - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.5.8 | 3 | 6 | AO |  |  | C | 12.1.5 | FV1211 FG quenc. wat.util. to NZ1111 - req.pos. |  | FV1211 | P30 | FV | 1211 |  | _ | 10 | ZY | P30FV1211_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00416 | 416 |  | P30FV1212_ZSL | vlv. FV1212 FG quenc. wat.util. to NZ1112 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 9 | 19 | DI |  |  | C | 12.1.7 | FV1212 FG quenc. wat.util. to NZ1112 - closed |  | FV1212 | P30 | FV | 1212 |  | _ | 10 | ZSL | P30FV1212_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00417 | 417 |  | P30FV1212_ZY | vlv. FV1212 FG quenc. wat.util. to NZ1112 - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.5.8 | 4 | 6 | AO |  |  | C | 12.1.5 | FV1212 FG quenc. wat.util. to NZ1112 - req.pos. |  | FV1212 | P30 | FV | 1212 |  | _ | 10 | ZY | P30FV1212_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00418 | 418 |  | P30FV1301_ZSL | vlv. FV1301 FG quenc. compr.air to nebul - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 10 | 19 | DI |  |  | C | 12.1.7 | FV1301 FG quenc. compr.air to nebul - closed |  | FV1301 | P30 | FV | 1301 |  | _ | 10 | ZSL | P30FV1301_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00419 | 419 |  | P30FV1301_ZY | vlv. FV1301 FG quenc. compr.air to nebul - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.5.8 | 5 | 6 | AO |  |  | C | 12.1.5 | FV1301 FG quenc. compr.air to nebul - req.pos. |  | FV1301 | P30 | FV | 1301 |  | _ | 10 | ZY | P30FV1301_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00420 | 420 |  | P30LSLL1200 | lev. LL LSLL1200 FG quenc. wat.util. TK1200 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.7.2 | 11 | 19 | DI |  |  | C | 12.1.7 | LL LSLL1200 FG quenc. wat.util. TK1200 |  | LL | P30 | LSLL | 1200 |  |  |  |  | P30LSLL1200 | ok | [5 empty] | 0
ID-S01AP1030-00421 | 421 |  | P30LI1200 | lev. LT1200 FG quenc. wat.util. TK1200 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  | 12 |  | 12.1.6.3 | 8 | 15 | AI |  |  | C | 12.1.6 | LT1200 FG quenc. wat.util. TK1200 |  | LT1200 | P30 | LI | 1200 |  |  |  |  | P30LI1200 | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00422 | 422 |  | P30PM1200A_YLRE | pump PM1200A FG quenc. wat.util. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.1 | 19 | 28 | DI |  |  | C | 12.1.5 | PM1200A FG quenc. wat.util. - in remote |  | PM1200A | P30 | PM | 1200 | A | _ | 11 | YLRE | P30PM1200A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00423 | 423 |  | P30PM1200A_YLH | pump PM1200A FG quenc. wat.util. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.1 | 20 | 28 | DI |  |  | C | 12.1.5 | PM1200A FG quenc. wat.util. - in running |  | PM1200A | P30 | PM | 1200 | A | _ | 11 | YLH | P30PM1200A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00424 | 424 |  | P30PM1200A_YSG | pump PM1200A FG quenc. wat.util. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.1 | 21 | 28 | DI |  |  | C | 12.1.5 | PM1200A FG quenc. wat.util. - supply fault |  | PM1200A | P30 | PM | 1200 | A | _ | 11 | YSG | P30PM1200A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00425 | 425 |  | P30PM1200A_HSH | pump PM1200A FG quenc. wat.util. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 11 | 31 | DO |  |  | C | 12.1.5 | PM1200A FG quenc. wat.util. - start/stop |  | PM1200A | P30 | PM | 1200 | A | _ | 11 | HSH | P30PM1200A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00426 | 426 |  | P30PM1200B_YLRE | pump PM1200B FG quenc. wat.util. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.6 | 19 | 24 | DI |  |  | C | 12.1.6 | PM1200B FG quenc. wat.util. - in remote |  | PM1200B | P30 | PM | 1200 | B | _ | 11 | YLRE | P30PM1200B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00427 | 427 |  | P30PM1200B_YLH | pump PM1200B FG quenc. wat.util. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.6 | 20 | 24 | DI |  |  | C | 12.1.6 | PM1200B FG quenc. wat.util. - in running |  | PM1200B | P30 | PM | 1200 | B | _ | 11 | YLH | P30PM1200B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00428 | 428 |  | P30PM1200B_YSG | pump PM1200B FG quenc. wat.util. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 21 | 24 | DI |  |  | C | 12.1.6 | PM1200B FG quenc. wat.util. - supply fault |  | PM1200B | P30 | PM | 1200 | B | _ | 11 | YSG | P30PM1200B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00429 | 429 |  | P30PM1200B_HSH | pump PM1200B FG quenc. wat.util. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | P30MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 12 | 31 | DO |  |  | C | 12.1.5 | PM1200B FG quenc. wat.util. - start/stop |  | PM1200B | P30 | PM | 1200 | B | _ | 11 | HSH | P30PM1200B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00430 | 430 |  | P30POV1100_ZSH | vlv. POV1100 FG quenc. inlet QT1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 12 | 19 | DI |  |  | C | 12.1.7 | POV1100 FG quenc. inlet QT1100 - opened |  | POV1100 | P30 | POV | 1100 |  | _ | 11 | ZSH | P30POV1100_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00431 | 431 |  | P30POV1100_ZSL | vlv. POV1100 FG quenc. inlet QT1100 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 13 | 19 | DI |  |  | C | 12.1.7 | POV1100 FG quenc. inlet QT1100 - closed |  | POV1100 | P30 | POV | 1100 |  | _ | 11 | ZSL | P30POV1100_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00432 | 432 |  | P30POV1100_HSH | vlv. POV1100 FG quenc. inlet QT1100 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 22 | 30 | DO |  |  | C | 12.1.6 | POV1100 FG quenc. inlet QT1100 - open |  | POV1100 | P30 | POV | 1100 |  | _ | 11 | HSH | P30POV1100_HSH | ok | [5 empty] | 0
ID-S01AP1030-00433 | 433 |  | P30POV1100_HSL | vlv. POV1100 FG quenc. inlet QT1100 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 23 | 30 | DO |  |  | C | 12.1.6 | POV1100 FG quenc. inlet QT1100 - close |  | POV1100 | P30 | POV | 1100 |  | _ | 11 | HSL | P30POV1100_HSL | ok | [5 empty] | 0
ID-S01AP1030-00434 | 434 |  | P30POV1200_ZSH | vlv. POV1200 filling FG quenc. wat.util. TK1200 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 14 | 19 | DI |  |  | C | 12.1.7 | POV1200 filling FG quenc. wat.util. TK1200 - opened |  | POV1200 | P30 | POV | 1200 |  | _ | 11 | ZSH | P30POV1200_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00435 | 435 |  | P30POV1200_ZSL | vlv. POV1200 filling FG quenc. wat.util. TK1200 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 15 | 19 | DI |  |  | C | 12.1.7 | POV1200 filling FG quenc. wat.util. TK1200 - closed |  | POV1200 | P30 | POV | 1200 |  | _ | 11 | ZSL | P30POV1200_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00436 | 436 |  | P30POV1200_HSH | vlv. POV1200 filling FG quenc. wat.util. TK1200 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 24 | 30 | DO |  |  | C | 12.1.6 | POV1200 filling FG quenc. wat.util. TK1200 - open |  | POV1200 | P30 | POV | 1200 |  | _ | 11 | HSH | P30POV1200_HSH | ok | [5 empty] | 0
ID-S01AP1030-00437 | 437 |  | P30POV1200_HSL | vlv. POV1200 filling FG quenc. wat.util. TK1200 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 25 | 30 | DO |  |  | C | 12.1.6 | POV1200 filling FG quenc. wat.util. TK1200 - close |  | POV1200 | P30 | POV | 1200 |  | _ | 11 | HSL | P30POV1200_HSL | ok | [5 empty] | 0
ID-S01AP1030-00438 | 438 |  | P30POV1202_ZSH | vlv. POV1202 block FG quenc. wat.util. - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 16 | 19 | DI |  |  | C | 12.1.7 | POV1202 block FG quenc. wat.util. - opened |  | POV1202 | P30 | POV | 1202 |  | _ | 11 | ZSH | P30POV1202_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00439 | 439 |  | P30POV1202_ZSL | vlv. POV1202 block FG quenc. wat.util. - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 17 | 19 | DI |  |  | C | 12.1.7 | POV1202 block FG quenc. wat.util. - closed |  | POV1202 | P30 | POV | 1202 |  | _ | 11 | ZSL | P30POV1202_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00440 | 440 |  | P30POV1202_HSH | vlv. POV1202 block FG quenc. wat.util. - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 26 | 30 | DO |  |  | C | 12.1.6 | POV1202 block FG quenc. wat.util. - open |  | POV1202 | P30 | POV | 1202 |  | _ | 11 | HSH | P30POV1202_HSH | ok | [5 empty] | 0
ID-S01AP1030-00441 | 441 |  | P30POV1202_HSL | vlv. POV1202 block FG quenc. wat.util. - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 27 | 30 | DO |  |  | C | 12.1.6 | POV1202 block FG quenc. wat.util. - close |  | POV1202 | P30 | POV | 1202 |  | _ | 11 | HSL | P30POV1202_HSL | ok | [5 empty] | 0
ID-S01AP1030-00442 | 442 |  | P30POV1300_ZSH | vlv. POV1300 block FG quenc. compr.air - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 18 | 19 | DI |  |  | C | 12.1.7 | POV1300 block FG quenc. compr.air - opened |  | POV1300 | P30 | POV | 1300 |  | _ | 11 | ZSH | P30POV1300_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00443 | 443 |  | P30POV1300_ZSL | vlv. POV1300 block FG quenc. compr.air - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.7.2 | 19 | 19 | DI |  |  | C | 12.1.7 | POV1300 block FG quenc. compr.air - closed |  | POV1300 | P30 | POV | 1300 |  | _ | 11 | ZSL | P30POV1300_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00444 | 444 |  | P30POV1300_HSH | vlv. POV1300 block FG quenc. compr.air - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 28 | 30 | DO |  |  | C | 12.1.6 | POV1300 block FG quenc. compr.air - open |  | POV1300 | P30 | POV | 1300 |  | _ | 11 | HSH | P30POV1300_HSH | ok | [5 empty] | 0
ID-S01AP1030-00445 | 445 |  | P30POV1300_HSL | vlv. POV1300 block FG quenc. compr.air - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 29 | 30 | DO |  |  | C | 12.1.6 | POV1300 block FG quenc. compr.air - close |  | POV1300 | P30 | POV | 1300 |  | _ | 11 | HSL | P30POV1300_HSL | ok | [5 empty] | 0
ID-S01AP1030-00446 | 446 |  | P30POV1310_ZSH | vlv. POV1310 FG quenc. compr.air to NZ1110 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 1 | 27 | DI |  |  | C | 12.1.8 | POV1310 FG quenc. compr.air to NZ1110 - opened |  | POV1310 | P30 | POV | 1310 |  | _ | 11 | ZSH | P30POV1310_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00447 | 447 |  | P30POV1310_ZSL | vlv. POV1310 FG quenc. compr.air to NZ1110 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 2 | 27 | DI |  |  | C | 12.1.8 | POV1310 FG quenc. compr.air to NZ1110 - closed |  | POV1310 | P30 | POV | 1310 |  | _ | 11 | ZSL | P30POV1310_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00448 | 448 |  | P30POV1310_HSH | vlv. POV1310 FG quenc. compr.air to NZ1110 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.6.5 | 30 | 30 | DO |  |  | C | 12.1.6 | POV1310 FG quenc. compr.air to NZ1110 - open |  | POV1310 | P30 | POV | 1310 |  | _ | 11 | HSH | P30POV1310_HSH | ok | [5 empty] | 0
ID-S01AP1030-00449 | 449 |  | P30POV1310_HSL | vlv. POV1310 FG quenc. compr.air to NZ1110 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 1 | 32 | DO |  |  | C | 12.1.7 | POV1310 FG quenc. compr.air to NZ1110 - close |  | POV1310 | P30 | POV | 1310 |  | _ | 11 | HSL | P30POV1310_HSL | ok | [5 empty] | 0
ID-S01AP1030-00450 | 450 |  | P30POV1311_ZSH | vlv. POV1311 FG quenc. compr.air to NZ1111 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 3 | 27 | DI |  |  | C | 12.1.8 | POV1311 FG quenc. compr.air to NZ1111 - opened |  | POV1311 | P30 | POV | 1311 |  | _ | 11 | ZSH | P30POV1311_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00451 | 451 |  | P30POV1311_ZSL | vlv. POV1311 FG quenc. compr.air to NZ1111 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 4 | 27 | DI |  |  | C | 12.1.8 | POV1311 FG quenc. compr.air to NZ1111 - closed |  | POV1311 | P30 | POV | 1311 |  | _ | 11 | ZSL | P30POV1311_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00452 | 452 |  | P30POV1311_HSH | vlv. POV1311 FG quenc. compr.air to NZ1111 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 2 | 32 | DO |  |  | C | 12.1.7 | POV1311 FG quenc. compr.air to NZ1111 - open |  | POV1311 | P30 | POV | 1311 |  | _ | 11 | HSH | P30POV1311_HSH | ok | [5 empty] | 0
ID-S01AP1030-00453 | 453 |  | P30POV1311_HSL | vlv. POV1311 FG quenc. compr.air to NZ1111 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 3 | 32 | DO |  |  | C | 12.1.7 | POV1311 FG quenc. compr.air to NZ1111 - close |  | POV1311 | P30 | POV | 1311 |  | _ | 11 | HSL | P30POV1311_HSL | ok | [5 empty] | 0
ID-S01AP1030-00454 | 454 |  | P30POV1312_ZSH | vlv. POV1312 FG quenc. compr.air to NZ1112 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 5 | 27 | DI |  |  | C | 12.1.8 | POV1312 FG quenc. compr.air to NZ1112 - opened |  | POV1312 | P30 | POV | 1312 |  | _ | 11 | ZSH | P30POV1312_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00455 | 455 |  | P30POV1312_ZSL | vlv. POV1312 FG quenc. compr.air to NZ1112 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 6 | 27 | DI |  |  | C | 12.1.8 | POV1312 FG quenc. compr.air to NZ1112 - closed |  | POV1312 | P30 | POV | 1312 |  | _ | 11 | ZSL | P30POV1312_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00456 | 456 |  | P30POV1312_HSH | vlv. POV1312 FG quenc. compr.air to NZ1112 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 4 | 32 | DO |  |  | C | 12.1.7 | POV1312 FG quenc. compr.air to NZ1112 - open |  | POV1312 | P30 | POV | 1312 |  | _ | 11 | HSH | P30POV1312_HSH | ok | [5 empty] | 0
ID-S01AP1030-00457 | 457 |  | P30POV1312_HSL | vlv. POV1312 FG quenc. compr.air to NZ1112 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 5 | 32 | DO |  |  | C | 12.1.7 | POV1312 FG quenc. compr.air to NZ1112 - close |  | POV1312 | P30 | POV | 1312 |  | _ | 11 | HSL | P30POV1312_HSL | ok | [5 empty] | 0
ID-S01AP1030-00458 | 458 |  | P30PI1100 | press. PT1100 FG quenc. inlet QT1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-003 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | -1500 | ¸ | 0 | mmH20 |  | 12 |  | 12.1.6.3 | 9 | 15 | AI |  |  | C | 12.1.6 | PT1100 FG quenc. inlet QT1100 |  | PT1100 | P30 | PI | 1100 |  |  |  |  | P30PI1100 | ok |  |  |  | -1500 | 0 | mmH20
ID-S01AP1030-00459 | 459 |  | P30PI1300 | press. PT1300 FG quenc. compr.air PRV1300 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 10 | barG |  | 12 |  | 12.1.6.3 | 10 | 15 | AI |  |  | C | 12.1.6 | PT1300 FG quenc. compr.air PRV1300 |  | PT1300 | P30 | PI | 1300 |  |  |  |  | P30PI1300 | ok |  |  |  | 0 | 10 | barG
ID-S01AP1030-00460 | 460 |  | P30PI1301 | press. PT1301 FG quenc. compr.air to nebul |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 10 | barG |  | 12 |  | 12.1.6.3 | 11 | 15 | AI |  |  | C | 12.1.6 | PT1301 FG quenc. compr.air to nebul |  | PT1301 | P30 | PI | 1301 |  |  |  |  | P30PI1301 | ok |  |  |  | 0 | 10 | barG
ID-S01AP1030-00461 | 461 |  | P30TSL1220 | temp. L TSL1220 FG quenc. ambient air |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.8 | 7 | 27 | DI |  |  | D | 12.1.8 | L TSL1220 FG quenc. ambient air |  | L | P30 | TSL | 1220 |  |  |  |  | P30TSL1220 | ok | [5 empty] | 0
ID-S01AP1030-00462 | 462 |  | P30TI1100 | temp. TT1100 FG quenc. inlet QT1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-003 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 600 | °C |  | 12 |  | 12.1.6.3 | 12 | 15 | AI |  |  | C | 12.1.6 | TT1100 FG quenc. inlet QT1100 |  | TT1100 | P30 | TI | 1100 |  |  |  |  | P30TI1100 | ok |  |  |  | 0 | 600 | °C
ID-S01AP1030-00463 | 463 |  | P30TI1101X | temp. TT1101X FG quenc. outlet QT1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 600 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1101X FG quenc. outlet QT1100 |  | TT1101X | P30 | TI | 1101 | X |  |  |  | P30TI1101X | ok |  |  |  | 0 | 600 | °C
ID-S01AP1030-00464 | 464 |  | P30TI1101Y | temp. TT1101Y FG quenc. outlet QT1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P30 DP01 | CHN1-TDZ2-P30-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 600 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1101Y FG quenc. outlet QT1100 |  | TT1101Y | P30 | TI | 1101 | Y |  |  |  | P30TI1101Y | ok |  |  |  | 0 | 600 | °C
ID-S01AP1030-00465 | 465 |  | P32EH1131_YLH | elec.heater EH1131 dry FG clean. Unit1 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.2.6 | 1 | 6 | DI |  |  | C | 12.1.2 | EH1131 dry FG clean. Unit1 - in running |  | EH1131 | P32 | EH | 1131 |  | _ | 10 | YLH | P32EH1131_YLH | ok | [5 empty] | 0
ID-S01AP1030-00466 | 466 |  | P32EH1131_YSG | elec.heater EH1131 dry FG clean. Unit1 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.2.6 | 2 | 6 | DI |  |  | C | 12.1.2 | EH1131 dry FG clean. Unit1 - supply fault |  | EH1131 | P32 | EH | 1131 |  | _ | 10 | YSG | P32EH1131_YSG | ok | [5 empty] | 0
ID-S01AP1030-00467 | 467 |  | P32EH1131_HSH | elec.heater EH1131 dry FG clean. Unit1 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 30 | 39 | DO |  |  | C | 12.1.2 | EH1131 dry FG clean. Unit1 - start/stop |  | EH1131 | P32 | EH | 1131 |  | _ | 10 | HSH | P32EH1131_HSH | ok | [5 empty] | 0
ID-S01AP1030-00468 | 468 |  | P32EH1132_YLH | elec.heater EH1132 dry FG clean. Unit2 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.2.6 | 3 | 6 | DI |  |  | C | 12.1.2 | EH1132 dry FG clean. Unit2 - in running |  | EH1132 | P32 | EH | 1132 |  | _ | 10 | YLH | P32EH1132_YLH | ok | [5 empty] | 0
ID-S01AP1030-00469 | 469 |  | P32EH1132_YSG | elec.heater EH1132 dry FG clean. Unit2 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.2.6 | 4 | 6 | DI |  |  | C | 12.1.2 | EH1132 dry FG clean. Unit2 - supply fault |  | EH1132 | P32 | EH | 1132 |  | _ | 10 | YSG | P32EH1132_YSG | ok | [5 empty] | 0
ID-S01AP1030-00470 | 470 |  | P32EH1132_HSH | elec.heater EH1132 dry FG clean. Unit2 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 31 | 39 | DO |  |  | C | 12.1.2 | EH1132 dry FG clean. Unit2 - start/stop |  | EH1132 | P32 | EH | 1132 |  | _ | 10 | HSH | P32EH1132_HSH | ok | [5 empty] | 0
ID-S01AP1030-00471 | 471 |  | P32EH1133_YLH | elec.heater EH1133 dry FG clean. Unit3 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.2.6 | 5 | 6 | DI |  |  | C | 12.1.2 | EH1133 dry FG clean. Unit3 - in running |  | EH1133 | P32 | EH | 1133 |  | _ | 10 | YLH | P32EH1133_YLH | ok | [5 empty] | 0
ID-S01AP1030-00472 | 472 |  | P32EH1133_YSG | elec.heater EH1133 dry FG clean. Unit3 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.2.6 | 6 | 6 | DI |  |  | C | 12.1.2 | EH1133 dry FG clean. Unit3 - supply fault |  | EH1133 | P32 | EH | 1133 |  | _ | 10 | YSG | P32EH1133_YSG | ok | [5 empty] | 0
ID-S01AP1030-00473 | 473 |  | P32EH1133_HSH | elec.heater EH1133 dry FG clean. Unit3 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 32 | 39 | DO |  |  | C | 12.1.2 | EH1133 dry FG clean. Unit3 - start/stop |  | EH1133 | P32 | EH | 1133 |  | _ | 10 | HSH | P32EH1133_HSH | ok | [5 empty] | 0
ID-S01AP1030-00474 | 474 |  | P32EH1134_YLH | elec.heater EH1134 dry FG clean. Unit4 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 4 | 29 | DI |  |  | C | 12.1.3 | EH1134 dry FG clean. Unit4 - in running |  | EH1134 | P32 | EH | 1134 |  | _ | 10 | YLH | P32EH1134_YLH | ok | [5 empty] | 0
ID-S01AP1030-00475 | 475 |  | P32EH1134_YSG | elec.heater EH1134 dry FG clean. Unit4 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.1 | 5 | 29 | DI |  |  | C | 12.1.3 | EH1134 dry FG clean. Unit4 - supply fault |  | EH1134 | P32 | EH | 1134 |  | _ | 10 | YSG | P32EH1134_YSG | ok | [5 empty] | 0
ID-S01AP1030-00476 | 476 |  | P32EH1134_HSH | elec.heater EH1134 dry FG clean. Unit4 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 33 | 39 | DO |  |  | C | 12.1.2 | EH1134 dry FG clean. Unit4 - start/stop |  | EH1134 | P32 | EH | 1134 |  | _ | 10 | HSH | P32EH1134_HSH | ok | [5 empty] | 0
ID-S01AP1030-00477 | 477 |  | P32EH1152_YLH | elec.heater EH1152 dry FG clean. 1°stage - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 6 | 29 | DI |  |  | C | 12.1.3 | EH1152 dry FG clean. 1°stage - in running |  | EH1152 | P32 | EH | 1152 |  | _ | 10 | YLH | P32EH1152_YLH | ok | [5 empty] | 0
ID-S01AP1030-00478 | 478 |  | P32EH1152_YSG | elec.heater EH1152 dry FG clean. 1°stage - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.1 | 7 | 29 | DI |  |  | C | 12.1.3 | EH1152 dry FG clean. 1°stage - supply fault |  | EH1152 | P32 | EH | 1152 |  | _ | 10 | YSG | P32EH1152_YSG | ok | [5 empty] | 0
ID-S01AP1030-00479 | 479 |  | P32EH1152_HSH | elec.heater EH1152 dry FG clean. 1°stage - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 34 | 39 | DO |  |  | C | 12.1.2 | EH1152 dry FG clean. 1°stage - start/stop |  | EH1152 | P32 | EH | 1152 |  | _ | 10 | HSH | P32EH1152_HSH | ok | [5 empty] | 0
ID-S01AP1030-00480 | 480 |  | P32EH1153_YLH | elec.heater EH1153 dry FG clean. 2°stage - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 8 | 29 | DI |  |  | C | 12.1.3 | EH1153 dry FG clean. 2°stage - in running |  | EH1153 | P32 | EH | 1153 |  | _ | 10 | YLH | P32EH1153_YLH | ok | [5 empty] | 0
ID-S01AP1030-00481 | 481 |  | P32EH1153_YSG | elec.heater EH1153 dry FG clean. 2°stage - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.1 | 9 | 29 | DI |  |  | C | 12.1.3 | EH1153 dry FG clean. 2°stage - supply fault |  | EH1153 | P32 | EH | 1153 |  | _ | 10 | YSG | P32EH1153_YSG | ok | [5 empty] | 0
ID-S01AP1030-00482 | 482 |  | P32EH1153_HSH | elec.heater EH1153 dry FG clean. 2°stage - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 35 | 39 | DO |  |  | C | 12.1.2 | EH1153 dry FG clean. 2°stage - start/stop |  | EH1153 | P32 | EH | 1153 |  | _ | 10 | HSH | P32EH1153_HSH | ok | [5 empty] | 0
ID-S01AP1030-00483 | 483 |  | P32EH1154_YLH | elec.heater EH1154 dry FG clean. 3°stage - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 10 | 29 | DI |  |  | C | 12.1.3 | EH1154 dry FG clean. 3°stage - in running |  | EH1154 | P32 | EH | 1154 |  | _ | 10 | YLH | P32EH1154_YLH | ok | [5 empty] | 0
ID-S01AP1030-00484 | 484 |  | P32EH1154_YSG | elec.heater EH1154 dry FG clean. 3°stage - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.1 | 11 | 29 | DI |  |  | C | 12.1.3 | EH1154 dry FG clean. 3°stage - supply fault |  | EH1154 | P32 | EH | 1154 |  | _ | 10 | YSG | P32EH1154_YSG | ok | [5 empty] | 0
ID-S01AP1030-00485 | 485 |  | P32EH1154_HSH | elec.heater EH1154 dry FG clean. 3°stage - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 36 | 39 | DO |  |  | C | 12.1.2 | EH1154 dry FG clean. 3°stage - start/stop |  | EH1154 | P32 | EH | 1154 |  | _ | 10 | HSH | P32EH1154_HSH | ok | [5 empty] | 0
ID-S01AP1030-00486 | 486 |  | P32FN1151_YLRE | fan FN1151 preheat dry FG clean. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 12 | 29 | DI |  |  | C | 12.1.3 | FN1151 preheat dry FG clean. - in remote |  | FN1151 | P32 | FN | 1151 |  | _ | 10 | YLRE | P32FN1151_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00487 | 487 |  | P32FN1151_YLH | fan FN1151 preheat dry FG clean. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 13 | 29 | DI |  |  | C | 12.1.3 | FN1151 preheat dry FG clean. - in running |  | FN1151 | P32 | FN | 1151 |  | _ | 10 | YLH | P32FN1151_YLH | ok | [5 empty] | 0
ID-S01AP1030-00488 | 488 |  | P32FN1151_YSG | fan FN1151 preheat dry FG clean. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.1 | 14 | 29 | DI |  |  | C | 12.1.3 | FN1151 preheat dry FG clean. - supply fault |  | FN1151 | P32 | FN | 1151 |  | _ | 10 | YSG | P32FN1151_YSG | ok | [5 empty] | 0
ID-S01AP1030-00489 | 489 |  | P32FN1151_HSH | fan FN1151 preheat dry FG clean. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 37 | 39 | DO |  |  | C | 12.1.2 | FN1151 preheat dry FG clean. - start/stop |  | FN1151 | P32 | FN | 1151 |  | _ | 10 | HSH | P32FN1151_HSH | ok | [5 empty] | 0
ID-S01AP1030-00490 | 490 |  | P32HV1121_ZSH | vlv. HV1121 dry FG clean. dust from Unit1 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 8 | 27 | DI |  |  | C | 12.1.8 | HV1121 dry FG clean. dust from Unit1 - opened |  | HV1121 | P32 | HV | 1121 |  | _ | 10 | ZSH | P32HV1121_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00491 | 491 |  | P32HV1122_ZSH | vlv. HV1122 dry FG clean. dust from Unit2 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 9 | 27 | DI |  |  | C | 12.1.8 | HV1122 dry FG clean. dust from Unit2 - opened |  | HV1122 | P32 | HV | 1122 |  | _ | 10 | ZSH | P32HV1122_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00492 | 492 |  | P32HV1123_ZSH | vlv. HV1123 dry FG clean. dust from Unit3 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 10 | 27 | DI |  |  | C | 12.1.8 | HV1123 dry FG clean. dust from Unit3 - opened |  | HV1123 | P32 | HV | 1123 |  | _ | 10 | ZSH | P32HV1123_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00493 | 493 |  | P32HV1124_ZSH | vlv. HV1124 dry FG clean. dust from Unit4 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 11 | 27 | DI |  |  | C | 12.1.8 | HV1124 dry FG clean. dust from Unit4 - opened |  | HV1124 | P32 | HV | 1124 |  | _ | 10 | ZSH | P32HV1124_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00494 | 494 |  | P32CD1110_YLH | aut.pan. AP1110 cleaning dry FG clean. FF1101 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | in marcia | 0 |  | 12 |  | 12.1.4.8 | 11 | 26 | DI |  |  | C | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - in running |  | AP1110 | P32 | CD | 1110 |  | _ | 10 | YLH | P32CD1110_YLH | ok | [5 empty] | 0
ID-S01AP1030-00495 | 495 |  | P32CD1110_YLRE | aut.pan. AP1110 cleaning dry FG clean. FF1101 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | in remoto | 0 |  | 12 |  | 12.1.4.8 | 12 | 26 | DI |  |  | C | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - in remote |  | AP1110 | P32 | CD | 1110 |  | _ | 10 | YLRE | P32CD1110_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00496 | 496 |  | P32CD1110_YSA | aut.pan. AP1110 cleaning dry FG clean. FF1101 - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | allarme | 0 |  | 12 |  | 12.1.4.8 | 13 | 26 | DI |  |  | C | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - com.alarm |  | AP1110 | P32 | CD | 1110 |  | _ | 10 | YSA | P32CD1110_YSA | ok | [5 empty] | 0
ID-S01AP1030-00497 | 497 |  | P32CD1111_YSA | aut.pan. AP1110 cleaning dry FG clean. FF1101 - start check alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | allarme | 0 |  | 12 |  | 12.1.4.8 | 14 | 26 | DI |  |  | D | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - start check alarm |  | AP1110 | P32 | CD | 1111 |  | _ | 10 | YSA | P32CD1111_YSA | ok | [5 empty] | 0
ID-S01AP1030-00498 | 498 |  | P32CD1112_YSA | aut.pan. AP1110 cleaning dry FG clean. FF1101 - ev stopped |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | allarme | 0 |  | 12 |  | 12.1.4.8 | 15 | 26 | DI |  |  | D | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - ev stopped |  | AP1110 | P32 | CD | 1112 |  | _ | 10 | YSA | P32CD1112_YSA | ok | [5 empty] | 0
ID-S01AP1030-00499 | 499 |  | P32CD1110_HSH | aut.pan. AP1110 cleaning dry FG clean. FF1101 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | marcia | 0 |  | 12 |  | 12.1.4.5 | 21 | 31 | DO |  |  | C | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - start/stop |  | AP1110 | P32 | CD | 1110 |  | _ | 10 | HSH | P32CD1110_HSH | ok | [5 empty] | 0
ID-S01AP1030-00500 | 500 |  | P32CD1111_HSH | aut.pan. AP1110 cleaning dry FG clean. FF1101 - disable unit 1 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | disabilita | 0 |  | 12 |  | 12.1.4.5 | 22 | 31 | DO |  |  | D | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - disable unit 1 |  | AP1110 | P32 | CD | 1111 |  | _ | 10 | HSH | P32CD1111_HSH | ok | [5 empty] | 0
ID-S01AP1030-00501 | 501 |  | P32CD1112_HSH | aut.pan. AP1110 cleaning dry FG clean. FF1101 - disable unit 2 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | disabilita | 0 |  | 12 |  | 12.1.4.5 | 23 | 31 | DO |  |  | D | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - disable unit 2 |  | AP1110 | P32 | CD | 1112 |  | _ | 10 | HSH | P32CD1112_HSH | ok | [5 empty] | 0
ID-S01AP1030-00502 | 502 |  | P32CD1113_HSH | aut.pan. AP1110 cleaning dry FG clean. FF1101 - disable unit 3 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | disabilita | 0 |  | 12 |  | 12.1.4.5 | 24 | 31 | DO |  |  | D | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - disable unit 3 |  | AP1110 | P32 | CD | 1113 |  | _ | 10 | HSH | P32CD1113_HSH | ok | [5 empty] | 0
ID-S01AP1030-00503 | 503 |  | P32CD1114_HSH | aut.pan. AP1110 cleaning dry FG clean. FF1101 - disable unit 4 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | disabilita | 0 |  | 12 |  | 12.1.4.5 | 25 | 31 | DO |  |  | D | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - disable unit 4 |  | AP1110 | P32 | CD | 1114 |  | _ | 10 | HSH | P32CD1114_HSH | ok | [5 empty] | 0
ID-S01AP1030-00504 | 504 |  | P32CD1115_HSH | aut.pan. AP1110 cleaning dry FG clean. FF1101 - sel. man/auto mode |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | automatico | 0 |  | 12 |  | 12.1.4.5 | 26 | 31 | DO |  |  | D | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - sel. man/auto mode |  | AP1110 | P32 | CD | 1115 |  | _ | 10 | HSH | P32CD1115_HSH | ok | [5 empty] | 0
ID-S01AP1030-00505 | 505 |  | P32CD1116_HSH | aut.pan. AP1110 cleaning dry FG clean. FF1101 - sel. startup/shutdown mode |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | avviamento | 0 |  | 12 |  | 12.1.4.5 | 27 | 31 | DO |  |  | D | 12.1.4 | AP1110 cleaning dry FG clean. FF1101 - sel. startup/shutdown mode |  | AP1110 | P32 | CD | 1116 |  | _ | 10 | HSH | P32CD1116_HSH | ok | [5 empty] | 0
ID-S01AP1030-00506 | 506 |  | P32CD1110_PDI | aut.pan. AP1110 cleaning dry FG clean. FF1101 - Pressure drop Bag filter |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | mmH20 |  | 12 |  | 12.1.2.2 | 1 | 2 | AI |  |  | D | 12.1.2 | AP1110 cleaning dry FG clean. FF1101 - Pressure drop Bag filter |  | AP1110 | P32 | CD | 1110 |  | _ | 10 | PDI | P32CD1110_PDI | ok |  |  |  | 0 | 300 | mmH20
ID-S01AP1030-00507 | 507 | P32CD110_AI | P32CD1110_AI | aut.pan. AP1110 cleaning dry FG clean. FF1101 - Dust oulet Bag filter |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | mg/nm3 |  | 12 |  | 12.1.2.2 | 2 | 2 | AI |  |  | D | 12.1.2 | AP1110 cleaning dry FG clean. FF1101 - Dust oulet Bag filter |  | AP1110 | P32 | CD | 1110 |  | _ | 10 | AI | P32CD1110_AI | ok |  |  |  | 0 | 100 | mg/nm3
ID-S01AP1030-00508 | 508 |  | P32CD1110_PDY | aut.pan. AP1110 cleaning dry FG clean. FF1101 - SetPoint pressure drop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.8 | 7 | 8 | AO |  |  | C | 12.1.1 | AP1110 cleaning dry FG clean. FF1101 - SetPoint pressure drop |  | AP1110 | P32 | CD | 1110 |  | _ | 10 | PDY | P32CD1110_PDY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00509 | 509 |  | P32TSL1101 | temp. L TSL1101 dry FG clean. hopper Unit1 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.8 | 12 | 27 | DI |  |  | D | 12.1.8 | L TSL1101 dry FG clean. hopper Unit1 |  | L | P32 | TSL | 1101 |  |  |  |  | P32TSL1101 | ok | [5 empty] | 0
ID-S01AP1030-00510 | 510 |  | P32TSL1102 | temp. L TSL1102 dry FG clean. hopper Unit2 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.8 | 13 | 27 | DI |  |  | D | 12.1.8 | L TSL1102 dry FG clean. hopper Unit2 |  | L | P32 | TSL | 1102 |  |  |  |  | P32TSL1102 | ok | [5 empty] | 0
ID-S01AP1030-00511 | 511 |  | P32TSL1103 | temp. L TSL1103 dry FG clean. hopper Unit3 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.8 | 14 | 27 | DI |  |  | D | 12.1.8 | L TSL1103 dry FG clean. hopper Unit3 |  | L | P32 | TSL | 1103 |  |  |  |  | P32TSL1103 | ok | [5 empty] | 0
ID-S01AP1030-00512 | 512 |  | P32TSL1104 | temp. L TSL1104 dry FG clean. hopper Unit4 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.8 | 15 | 27 | DI |  |  | D | 12.1.8 | L TSL1104 dry FG clean. hopper Unit4 |  | L | P32 | TSL | 1104 |  |  |  |  | P32TSL1104 | ok | [5 empty] | 0
ID-S01AP1030-00513 | 513 |  | P32POV1101_ZSH | vlv. POV1101 dry FG clean. inlet FF1101 Unit1 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 16 | 27 | DI |  |  | C | 12.1.8 | POV1101 dry FG clean. inlet FF1101 Unit1 - opened |  | POV1101 | P32 | POV | 1101 |  | _ | 11 | ZSH | P32POV1101_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00514 | 514 |  | P32POV1101_ZSL | vlv. POV1101 dry FG clean. inlet FF1101 Unit1 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 17 | 27 | DI |  |  | C | 12.1.8 | POV1101 dry FG clean. inlet FF1101 Unit1 - closed |  | POV1101 | P32 | POV | 1101 |  | _ | 11 | ZSL | P32POV1101_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00515 | 515 |  | P32POV1101_HSH | vlv. POV1101 dry FG clean. inlet FF1101 Unit1 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 6 | 32 | DO |  |  | C | 12.1.7 | POV1101 dry FG clean. inlet FF1101 Unit1 - open |  | POV1101 | P32 | POV | 1101 |  | _ | 11 | HSH | P32POV1101_HSH | ok | [5 empty] | 0
ID-S01AP1030-00516 | 516 |  | P32POV1101_HSL | vlv. POV1101 dry FG clean. inlet FF1101 Unit1 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 7 | 32 | DO |  |  | C | 12.1.7 | POV1101 dry FG clean. inlet FF1101 Unit1 - close |  | POV1101 | P32 | POV | 1101 |  | _ | 11 | HSL | P32POV1101_HSL | ok | [5 empty] | 0
ID-S01AP1030-00517 | 517 |  | P32POV1102_ZSH | vlv. POV1102 dry FG clean. inlet FF1101 Unit2 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 18 | 27 | DI |  |  | C | 12.1.8 | POV1102 dry FG clean. inlet FF1101 Unit2 - opened |  | POV1102 | P32 | POV | 1102 |  | _ | 11 | ZSH | P32POV1102_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00518 | 518 |  | P32POV1102_ZSL | vlv. POV1102 dry FG clean. inlet FF1101 Unit2 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 19 | 27 | DI |  |  | C | 12.1.8 | POV1102 dry FG clean. inlet FF1101 Unit2 - closed |  | POV1102 | P32 | POV | 1102 |  | _ | 11 | ZSL | P32POV1102_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00519 | 519 |  | P32POV1102_HSH | vlv. POV1102 dry FG clean. inlet FF1101 Unit2 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 8 | 32 | DO |  |  | C | 12.1.7 | POV1102 dry FG clean. inlet FF1101 Unit2 - open |  | POV1102 | P32 | POV | 1102 |  | _ | 11 | HSH | P32POV1102_HSH | ok | [5 empty] | 0
ID-S01AP1030-00520 | 520 |  | P32POV1102_HSL | vlv. POV1102 dry FG clean. inlet FF1101 Unit2 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 9 | 32 | DO |  |  | C | 12.1.7 | POV1102 dry FG clean. inlet FF1101 Unit2 - close |  | POV1102 | P32 | POV | 1102 |  | _ | 11 | HSL | P32POV1102_HSL | ok | [5 empty] | 0
ID-S01AP1030-00521 | 521 |  | P32POV1103_ZSH | vlv. POV1103 dry FG clean. inlet FF1101 Unit3 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 20 | 27 | DI |  |  | C | 12.1.8 | POV1103 dry FG clean. inlet FF1101 Unit3 - opened |  | POV1103 | P32 | POV | 1103 |  | _ | 11 | ZSH | P32POV1103_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00522 | 522 |  | P32POV1103_ZSL | vlv. POV1103 dry FG clean. inlet FF1101 Unit3 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 21 | 27 | DI |  |  | C | 12.1.8 | POV1103 dry FG clean. inlet FF1101 Unit3 - closed |  | POV1103 | P32 | POV | 1103 |  | _ | 11 | ZSL | P32POV1103_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00523 | 523 |  | P32POV1103_HSH | vlv. POV1103 dry FG clean. inlet FF1101 Unit3 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 10 | 32 | DO |  |  | C | 12.1.7 | POV1103 dry FG clean. inlet FF1101 Unit3 - open |  | POV1103 | P32 | POV | 1103 |  | _ | 11 | HSH | P32POV1103_HSH | ok | [5 empty] | 0
ID-S01AP1030-00524 | 524 |  | P32POV1103_HSL | vlv. POV1103 dry FG clean. inlet FF1101 Unit3 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 11 | 32 | DO |  |  | C | 12.1.7 | POV1103 dry FG clean. inlet FF1101 Unit3 - close |  | POV1103 | P32 | POV | 1103 |  | _ | 11 | HSL | P32POV1103_HSL | ok | [5 empty] | 0
ID-S01AP1030-00525 | 525 |  | P32POV1104_ZSH | vlv. POV1104 dry FG clean. inlet FF1101 Unit4 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 22 | 27 | DI |  |  | C | 12.1.8 | POV1104 dry FG clean. inlet FF1101 Unit4 - opened |  | POV1104 | P32 | POV | 1104 |  | _ | 11 | ZSH | P32POV1104_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00526 | 526 |  | P32POV1104_ZSL | vlv. POV1104 dry FG clean. inlet FF1101 Unit4 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 23 | 27 | DI |  |  | C | 12.1.8 | POV1104 dry FG clean. inlet FF1101 Unit4 - closed |  | POV1104 | P32 | POV | 1104 |  | _ | 11 | ZSL | P32POV1104_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00527 | 527 |  | P32POV1104_HSH | vlv. POV1104 dry FG clean. inlet FF1101 Unit4 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 12 | 32 | DO |  |  | C | 12.1.7 | POV1104 dry FG clean. inlet FF1101 Unit4 - open |  | POV1104 | P32 | POV | 1104 |  | _ | 11 | HSH | P32POV1104_HSH | ok | [5 empty] | 0
ID-S01AP1030-00528 | 528 |  | P32POV1104_HSL | vlv. POV1104 dry FG clean. inlet FF1101 Unit4 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 13 | 32 | DO |  |  | C | 12.1.7 | POV1104 dry FG clean. inlet FF1101 Unit4 - close |  | POV1104 | P32 | POV | 1104 |  | _ | 11 | HSL | P32POV1104_HSL | ok | [5 empty] | 0
ID-S01AP1030-00529 | 529 |  | P32POV1115_ZSH | vlv. POV1115 dry FG clean. outlet FF1101 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 24 | 27 | DI |  |  | C | 12.1.8 | POV1115 dry FG clean. outlet FF1101 - opened |  | POV1115 | P32 | POV | 1115 |  | _ | 11 | ZSH | P32POV1115_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00530 | 530 |  | P32POV1115_ZSL | vlv. POV1115 dry FG clean. outlet FF1101 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 25 | 27 | DI |  |  | C | 12.1.8 | POV1115 dry FG clean. outlet FF1101 - closed |  | POV1115 | P32 | POV | 1115 |  | _ | 11 | ZSL | P32POV1115_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00531 | 531 |  | P32POV1115_HSH | vlv. POV1115 dry FG clean. outlet FF1101 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 14 | 32 | DO |  |  | C | 12.1.7 | POV1115 dry FG clean. outlet FF1101 - open |  | POV1115 | P32 | POV | 1115 |  | _ | 11 | HSH | P32POV1115_HSH | ok | [5 empty] | 0
ID-S01AP1030-00532 | 532 |  | P32POV1115_HSL | vlv. POV1115 dry FG clean. outlet FF1101 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 15 | 32 | DO |  |  | C | 12.1.7 | POV1115 dry FG clean. outlet FF1101 - close |  | POV1115 | P32 | POV | 1115 |  | _ | 11 | HSL | P32POV1115_HSL | ok | [5 empty] | 0
ID-S01AP1030-00533 | 533 |  | P32POV1116_ZSH | vlv. POV1116 dry FG clean. outlet FF1101 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 26 | 27 | DI |  |  | C | 12.1.8 | POV1116 dry FG clean. outlet FF1101 - opened |  | POV1116 | P32 | POV | 1116 |  | _ | 11 | ZSH | P32POV1116_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00534 | 534 |  | P32POV1116_ZSL | vlv. POV1116 dry FG clean. outlet FF1101 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.8 | 27 | 27 | DI |  |  | C | 12.1.8 | POV1116 dry FG clean. outlet FF1101 - closed |  | POV1116 | P32 | POV | 1116 |  | _ | 11 | ZSL | P32POV1116_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00535 | 535 |  | P32POV1116_HSH | vlv. POV1116 dry FG clean. outlet FF1101 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 16 | 32 | DO |  |  | C | 12.1.7 | POV1116 dry FG clean. outlet FF1101 - open |  | POV1116 | P32 | POV | 1116 |  | _ | 11 | HSH | P32POV1116_HSH | ok | [5 empty] | 0
ID-S01AP1030-00536 | 536 |  | P32POV1116_HSL | vlv. POV1116 dry FG clean. outlet FF1101 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 17 | 32 | DO |  |  | C | 12.1.7 | POV1116 dry FG clean. outlet FF1101 - close |  | POV1116 | P32 | POV | 1116 |  | _ | 11 | HSL | P32POV1116_HSL | ok | [5 empty] | 0
ID-S01AP1030-00537 | 537 |  | P32POV1150_ZSH | vlv. POV1150 preheat dry FG clean. inlet - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.7 | 10 | 28 | DI |  |  | C | 12.1.8 | POV1150 preheat dry FG clean. inlet - opened |  | POV1150 | P32 | POV | 1150 |  | _ | 11 | ZSH | P32POV1150_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00538 | 538 |  | P32POV1150_ZSL | vlv. POV1150 preheat dry FG clean. inlet - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.7 | 11 | 28 | DI |  |  | C | 12.1.8 | POV1150 preheat dry FG clean. inlet - closed |  | POV1150 | P32 | POV | 1150 |  | _ | 11 | ZSL | P32POV1150_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00539 | 539 |  | P32POV1150_HSH | vlv. POV1150 preheat dry FG clean. inlet - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 18 | 32 | DO |  |  | C | 12.1.7 | POV1150 preheat dry FG clean. inlet - open |  | POV1150 | P32 | POV | 1150 |  | _ | 11 | HSH | P32POV1150_HSH | ok | [5 empty] | 0
ID-S01AP1030-00540 | 540 |  | P32POV1150_HSL | vlv. POV1150 preheat dry FG clean. inlet - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 19 | 32 | DO |  |  | C | 12.1.7 | POV1150 preheat dry FG clean. inlet - close |  | POV1150 | P32 | POV | 1150 |  | _ | 11 | HSL | P32POV1150_HSL | ok | [5 empty] | 0
ID-S01AP1030-00541 | 541 |  | P32POV1155_ZSH | vlv. POV1155 preheat dry FG clean. outlet - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.7 | 12 | 28 | DI |  |  | C | 12.1.8 | POV1155 preheat dry FG clean. outlet - opened |  | POV1155 | P32 | POV | 1155 |  | _ | 11 | ZSH | P32POV1155_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00542 | 542 |  | P32POV1155_ZSL | vlv. POV1155 preheat dry FG clean. outlet - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.7 | 13 | 28 | DI |  |  | C | 12.1.8 | POV1155 preheat dry FG clean. outlet - closed |  | POV1155 | P32 | POV | 1155 |  | _ | 11 | ZSL | P32POV1155_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00543 | 543 |  | P32POV1155_HSH | vlv. POV1155 preheat dry FG clean. outlet - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 20 | 32 | DO |  |  | C | 12.1.7 | POV1155 preheat dry FG clean. outlet - open |  | POV1155 | P32 | POV | 1155 |  | _ | 11 | HSH | P32POV1155_HSH | ok | [5 empty] | 0
ID-S01AP1030-00544 | 544 |  | P32POV1155_HSL | vlv. POV1155 preheat dry FG clean. outlet - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 21 | 32 | DO |  |  | C | 12.1.7 | POV1155 preheat dry FG clean. outlet - close |  | POV1155 | P32 | POV | 1155 |  | _ | 11 | HSL | P32POV1155_HSL | ok | [5 empty] | 0
ID-S01AP1030-00545 | 545 |  | P32PSL1300 | pres. L PSL1300 dry FG clean. compr.air |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.7 | 14 | 28 | DI |  |  | C | 12.1.8 | L PSL1300 dry FG clean. compr.air |  | L | P32 | PSL | 1300 |  |  |  |  | P32PSL1300 | ok | [5 empty] | 0
ID-S01AP1030-00546 | 546 |  | P32PI1101 | press. PT1101 dry FG clean. outlet |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | -1500 | ¸ | 0 | mmH20 |  | 12 |  | 12.1.6.3 | 13 | 15 | AI |  |  | C | 12.1.6 | PT1101 dry FG clean. outlet |  | PT1101 | P32 | PI | 1101 |  |  |  |  | P32PI1101 | ok |  |  |  | -1500 | 0 | mmH20
ID-S01AP1030-00547 | 547 |  | P32RV1121_YLRE | rot.vlv. RV1121 dry FG clean. dust from Unit1 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 15 | 29 | DI | Based on P&ID should be RV1125 |  | C | 12.1.3 | RV1121 dry FG clean. dust from Unit1 - in remote |  | RV1121 | P32 | RV | 1121 |  | _ | 10 | YLRE | P32RV1121_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00548 | 548 |  | P32RV1121_YLH | rot.vlv. RV1121 dry FG clean. dust from Unit1 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 16 | 29 | DI | Based on P&ID should be RV1125 |  | C | 12.1.3 | RV1121 dry FG clean. dust from Unit1 - in running |  | RV1121 | P32 | RV | 1121 |  | _ | 10 | YLH | P32RV1121_YLH | ok | [5 empty] | 0
ID-S01AP1030-00549 | 549 |  | P32RV1121_YSG | rot.vlv. RV1121 dry FG clean. dust from Unit1 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.1 | 17 | 29 | DI | Based on P&ID should be RV1125 |  | C | 12.1.3 | RV1121 dry FG clean. dust from Unit1 - supply fault |  | RV1121 | P32 | RV | 1121 |  | _ | 10 | YSG | P32RV1121_YSG | ok | [5 empty] | 0
ID-S01AP1030-00550 | 550 |  | P32RV1121_HSH | rot.vlv. RV1121 dry FG clean. dust from Unit1 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 38 | 39 | DO | Based on P&ID should be RV1125 |  | C | 12.1.2 | RV1121 dry FG clean. dust from Unit1 - start/stop |  | RV1121 | P32 | RV | 1121 |  | _ | 10 | HSH | P32RV1121_HSH | ok | [5 empty] | 0
ID-S01AP1030-00551 | 551 |  | P32RV1122_YLRE | rot.vlv. RV1122 dry FG clean. dust from Unit2 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 18 | 29 | DI | Based on P&ID should be RV1126 |  | C | 12.1.3 | RV1122 dry FG clean. dust from Unit2 - in remote |  | RV1122 | P32 | RV | 1122 |  | _ | 10 | YLRE | P32RV1122_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00552 | 552 |  | P32RV1122_YLH | rot.vlv. RV1122 dry FG clean. dust from Unit2 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 19 | 29 | DI | Based on P&ID should be RV1126 |  | C | 12.1.3 | RV1122 dry FG clean. dust from Unit2 - in running |  | RV1122 | P32 | RV | 1122 |  | _ | 10 | YLH | P32RV1122_YLH | ok | [5 empty] | 0
ID-S01AP1030-00553 | 553 |  | P32RV1122_YSG | rot.vlv. RV1122 dry FG clean. dust from Unit2 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.1 | 20 | 29 | DI | Based on P&ID should be RV1126 |  | C | 12.1.3 | RV1122 dry FG clean. dust from Unit2 - supply fault |  | RV1122 | P32 | RV | 1122 |  | _ | 10 | YSG | P32RV1122_YSG | ok | [5 empty] | 0
ID-S01AP1030-00554 | 554 |  | P32RV1122_HSH | rot.vlv. RV1122 dry FG clean. dust from Unit2 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.2.5 | 39 | 39 | DO | Based on P&ID should be RV1126 |  | C | 12.1.2 | RV1122 dry FG clean. dust from Unit2 - start/stop |  | RV1122 | P32 | RV | 1122 |  | _ | 10 | HSH | P32RV1122_HSH | ok | [5 empty] | 0
ID-S01AP1030-00555 | 555 |  | P32RV1123_YLRE | rot.vlv. RV1123 dry FG clean. dust from Unit3 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 21 | 29 | DI | Based on P&ID should be RV1127 |  | C | 12.1.3 | RV1123 dry FG clean. dust from Unit3 - in remote |  | RV1123 | P32 | RV | 1123 |  | _ | 10 | YLRE | P32RV1123_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00556 | 556 |  | P32RV1123_YLH | rot.vlv. RV1123 dry FG clean. dust from Unit3 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 22 | 29 | DI | Based on P&ID should be RV1127 |  | C | 12.1.3 | RV1123 dry FG clean. dust from Unit3 - in running |  | RV1123 | P32 | RV | 1123 |  | _ | 10 | YLH | P32RV1123_YLH | ok | [5 empty] | 0
ID-S01AP1030-00557 | 557 |  | P32RV1123_YSG | rot.vlv. RV1123 dry FG clean. dust from Unit3 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.1 | 23 | 29 | DI | Based on P&ID should be RV1127 |  | C | 12.1.3 | RV1123 dry FG clean. dust from Unit3 - supply fault |  | RV1123 | P32 | RV | 1123 |  | _ | 10 | YSG | P32RV1123_YSG | ok | [5 empty] | 0
ID-S01AP1030-00558 | 558 |  | P32RV1123_HSH | rot.vlv. RV1123 dry FG clean. dust from Unit3 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 1 | 24 | DO | Based on P&ID should be RV1127 |  | C | 12.1.3 | RV1123 dry FG clean. dust from Unit3 - start/stop |  | RV1123 | P32 | RV | 1123 |  | _ | 10 | HSH | P32RV1123_HSH | ok | [5 empty] | 0
ID-S01AP1030-00559 | 559 |  | P32RV1124_YLRE | rot.vlv. RV1124 dry FG clean. dust from Unit4 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 24 | 29 | DI | Based on P&ID should be RV1128 |  | C | 12.1.3 | RV1124 dry FG clean. dust from Unit4 - in remote |  | RV1124 | P32 | RV | 1124 |  | _ | 10 | YLRE | P32RV1124_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00560 | 560 |  | P32RV1124_YLH | rot.vlv. RV1124 dry FG clean. dust from Unit4 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.1 | 25 | 29 | DI | Based on P&ID should be RV1128 |  | C | 12.1.3 | RV1124 dry FG clean. dust from Unit4 - in running |  | RV1124 | P32 | RV | 1124 |  | _ | 10 | YLH | P32RV1124_YLH | ok | [5 empty] | 0
ID-S01AP1030-00561 | 561 |  | P32RV1124_YSG | rot.vlv. RV1124 dry FG clean. dust from Unit4 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.1 | 26 | 29 | DI | Based on P&ID should be RV1128 |  | C | 12.1.3 | RV1124 dry FG clean. dust from Unit4 - supply fault |  | RV1124 | P32 | RV | 1124 |  | _ | 10 | YSG | P32RV1124_YSG | ok | [5 empty] | 0
ID-S01AP1030-00562 | 562 |  | P32RV1124_HSH | rot.vlv. RV1124 dry FG clean. dust from Unit4 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 2 | 24 | DO | Based on P&ID should be RV1128 |  | C | 12.1.3 | RV1124 dry FG clean. dust from Unit4 - start/stop |  | RV1124 | P32 | RV | 1124 |  | _ | 10 | HSH | P32RV1124_HSH | ok | [5 empty] | 0
ID-S01AP1030-00563 | 563 |  | P32SSL1125 | speed L SSL1125 dry FG clean. RV1125 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.7 | 15 | 28 | DI |  |  | C | 12.1.8 | L SSL1125 dry FG clean. RV1125 |  | L | P32 | SSL | 1125 |  |  |  |  | P32SSL1125 | ok | [5 empty] | 0
ID-S01AP1030-00564 | 564 |  | P32SSL1126 | speed L SSL1126 dry FG clean. RV1126 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.7 | 16 | 28 | DI |  |  | C | 12.1.8 | L SSL1126 dry FG clean. RV1126 |  | L | P32 | SSL | 1126 |  |  |  |  | P32SSL1126 | ok | [5 empty] | 0
ID-S01AP1030-00565 | 565 |  | P32SSL1127 | speed L SSL1127 dry FG clean. RV1127 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.7 | 17 | 28 | DI |  |  | C | 12.1.8 | L SSL1127 dry FG clean. RV1127 |  | L | P32 | SSL | 1127 |  |  |  |  | P32SSL1127 | ok | [5 empty] | 0
ID-S01AP1030-00566 | 566 |  | P32SSL1128 | speed L SSL1128 dry FG clean. RV1128 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.7 | 18 | 28 | DI |  |  | C | 12.1.8 | L SSL1128 dry FG clean. RV1128 |  | L | P32 | SSL | 1128 |  |  |  |  | P32SSL1128 | ok | [5 empty] | 0
ID-S01AP1030-00567 | 567 |  | P32TSHH1152 | temp. HH TSHH1152 preheat dry FG clean. heater |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.7 | 19 | 28 | DI |  |  | C | 12.1.8 | HH TSHH1152 preheat dry FG clean. heater |  | HH | P32 | TSHH | 1152 |  |  |  |  | P32TSHH1152 | ok | [5 empty] | 0
ID-S01AP1030-00568 | 568 |  | P32SOV1105_HSH | vlv. SOV1105 dry FG clean. hopper unit1 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 22 | 32 | DO |  |  | C | 12.1.7 | SOV1105 dry FG clean. hopper unit1 - open |  | SOV1105 | P32 | SOV | 1105 |  | _ | 11 | HSH | P32SOV1105_HSH | ok | [5 empty] | 0
ID-S01AP1030-00569 | 569 |  | P32SOV1106_HSH | vlv. SOV1105 dry FG clean. hopper unit2 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 23 | 32 | DO |  |  | C | 12.1.7 | SOV1105 dry FG clean. hopper unit2 - open |  | SOV1105 | P32 | SOV | 1106 |  | _ | 11 | HSH | P32SOV1106_HSH | ok | [5 empty] | 0
ID-S01AP1030-00570 | 570 |  | P32SOV1107_HSH | vlv. SOV1105 dry FG clean. hopper unit3 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 24 | 32 | DO |  |  | C | 12.1.7 | SOV1105 dry FG clean. hopper unit3 - open |  | SOV1105 | P32 | SOV | 1107 |  | _ | 11 | HSH | P32SOV1107_HSH | ok | [5 empty] | 0
ID-S01AP1030-00571 | 571 |  | P32SOV1108_HSH | vlv. SOV1105 dry FG clean. hopper unit4 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 25 | 32 | DO |  |  | C | 12.1.7 | SOV1105 dry FG clean. hopper unit4 - open |  | SOV1105 | P32 | SOV | 1108 |  | _ | 11 | HSH | P32SOV1108_HSH | ok | [5 empty] | 0
ID-S01AP1030-00572 | 572 |  | P32TI1100X | temp. TT1100X dry FG clean. inlet FF1101 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1100X dry FG clean. inlet FF1101 |  | TT1100X | P32 | TI | 1100 | X |  |  |  | P32TI1100X | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00573 | 573 |  | P32TI1100Y | temp. TT1100Y dry FG clean. inlet FF1101 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1100Y dry FG clean. inlet FF1101 |  | TT1100Y | P32 | TI | 1100 | Y |  |  |  | P32TI1100Y | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00574 | 574 |  | P32TI1105 | temp. TT1105 dry FG clean. outlet FF1101 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.6.3 | 14 | 15 | AI |  |  | C | 12.1.6 | TT1105 dry FG clean. outlet FF1101 |  | TT1105 | P32 | TI | 1105 |  |  |  |  | P32TI1105 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00575 | 575 |  | P32TI1131 | temp. TT1131 dry FG clean. hopper Unit1 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.6.3 | 15 | 15 | AI |  |  | C | 12.1.6 | TT1131 dry FG clean. hopper Unit1 |  | TT1131 | P32 | TI | 1131 |  |  |  |  | P32TI1131 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00576 | 576 |  | P32TI1132 | temp. TT1132 dry FG clean. hopper Unit1 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.7.6 | 1 | 14 | AI |  |  | C | 12.1.7 | TT1132 dry FG clean. hopper Unit1 |  | TT1132 | P32 | TI | 1132 |  |  |  |  | P32TI1132 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00577 | 577 |  | P32TI1133 | temp. TT1133 dry FG clean. hopper Unit1 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.7.6 | 2 | 14 | AI |  |  | C | 12.1.7 | TT1133 dry FG clean. hopper Unit1 |  | TT1133 | P32 | TI | 1133 |  |  |  |  | P32TI1133 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00578 | 578 |  | P32TI1134 | temp. TT1134 dry FG clean. hopper Unit1 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.7.6 | 3 | 14 | AI |  |  | C | 12.1.7 | TT1134 dry FG clean. hopper Unit1 |  | TT1134 | P32 | TI | 1134 |  |  |  |  | P32TI1134 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00579 | 579 |  | P32TI1152 | temp. TT1152 preheat dry FG clean. inlet |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-003 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.6.2 | 5 | 8 | AI |  |  | C | 12.1.6 | TT1152 preheat dry FG clean. inlet |  | TT1152 | P32 | TI | 1152 |  |  |  |  | P32TI1152 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00580 | 580 |  | P32TI1153 | temp. TT1153 preheat dry FG clean. outlet |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-003 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.6.2 | 6 | 8 | AI |  |  | C | 12.1.6 | TT1153 preheat dry FG clean. outlet |  | TT1153 | P32 | TI | 1153 |  |  |  |  | P32TI1153 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00581 | 581 |  | P32TV1100_ZSL | vlv. TV1100 dry FG clean. inlet amb. air - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.7 | 20 | 28 | DI |  |  | C | 12.1.8 | TV1100 dry FG clean. inlet amb. air - closed |  | TV1100 | P32 | TV | 1100 |  | _ | 10 | ZSL | P32TV1100_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00582 | 582 |  | P32TV1100_ZY | vlv. TV1100 dry FG clean. inlet amb. air - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-003 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.5.8 | 6 | 6 | AO |  |  | C | 12.1.5 | TV1100 dry FG clean. inlet amb. air - req.pos. |  | TV1100 | P32 | TV | 1100 |  | _ | 10 | ZY | P32TV1100_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00583 | 583 |  | P32TV1100_HSK | vlv. TV1100 dry FG clean. inlet amb. air - forced open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P32 DP01 | CHN1-TDZ2-P32-JBA-1-003 |  | S01AP1030 |  |  |  |  | DOS | RELAY - 24 Vac | false | → | open | % |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TV1100 dry FG clean. inlet amb. air - forced open |  | TV1100 | P32 | TV | 1100 |  | _ | 10 | HSK | P32TV1100_HSK | ok | [5 empty] | %
ID-S01AP1030-00584 | 584 |  | P33AI1100 | anal. AT1100 recirc. wet FG clean. wat. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 2000 | µSiemens | 220 Vac / .. | 12 |  | 12.1.7.6 | 4 | 14 | AI |  |  | H | 12.1.7 | AT1100 recirc. wet FG clean. wat. |  | AT1100 | P33 | AI | 1100 |  |  |  |  | P33AI1100 | ok |  |  |  | 0 | 2000 | µSiemens
ID-S01AP1030-00585 | 585 |  | P33AI1150 | anal. AT1150 recirc. wet FG clean. sod.hydr. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 2 | ¸ | 14 | pH | 220 Vac / .. | 12 |  | 12.1.7.6 | 5 | 14 | AI |  |  | H | 12.1.7 | AT1150 recirc. wet FG clean. sod.hydr. |  | AT1150 | P33 | AI | 1150 |  |  |  |  | P33AI1150 | ok |  |  |  | 2 | 14 | pH
ID-S01AP1030-00586 | 586 |  | P33AI1151 | anal. AT1151 wet FG clean. sod.hydr. to SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 2 | ¸ | 14 | pH | 220 Vac / .. | 12 |  | 12.1.7.6 | 6 | 14 | AI |  |  | H | 12.1.7 | AT1151 wet FG clean. sod.hydr. to SB1100 |  | AT1151 | P33 | AI | 1151 |  |  |  |  | P33AI1151 | ok |  |  |  | 2 | 14 | pH
ID-S01AP1030-00587 | 587 |  | P33EH1210_YLH | elec.heater EH1210 wet FG clean. TK1200 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 22 | 28 | DI |  |  | C | 12.1.5 | EH1210 wet FG clean. TK1200 - in running |  | EH1210 | P33 | EH | 1210 |  | _ | 10 | YLH | P33EH1210_YLH | ok | [5 empty] | 0
ID-S01AP1030-00588 | 588 |  | P33EH1210_YSG | elec.heater EH1210 wet FG clean. TK1200 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 23 | 28 | DI |  |  | C | 12.1.5 | EH1210 wet FG clean. TK1200 - supply fault |  | EH1210 | P33 | EH | 1210 |  | _ | 10 | YSG | P33EH1210_YSG | ok | [5 empty] | 0
ID-S01AP1030-00589 | 589 |  | P33EH1210_HSH | elec.heater EH1210 wet FG clean. TK1200 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 13 | 31 | DO |  |  | C | 12.1.5 | EH1210 wet FG clean. TK1200 - start/stop |  | EH1210 | P33 | EH | 1210 |  | _ | 10 | HSH | P33EH1210_HSH | ok | [5 empty] | 0
ID-S01AP1030-00590 | 590 |  | P33EH1211_YLH | elec.heater EH1211 wet FG clean. sod.hydr. piping - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.5.1 | 24 | 28 | DI |  |  | C | 12.1.5 | EH1211 wet FG clean. sod.hydr. piping - in running |  | EH1211 | P33 | EH | 1211 |  | _ | 10 | YLH | P33EH1211_YLH | ok | [5 empty] | 0
ID-S01AP1030-00591 | 591 |  | P33EH1211_YSG | elec.heater EH1211 wet FG clean. sod.hydr. piping - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.5.1 | 25 | 28 | DI |  |  | C | 12.1.5 | EH1211 wet FG clean. sod.hydr. piping - supply fault |  | EH1211 | P33 | EH | 1211 |  | _ | 10 | YSG | P33EH1211_YSG | ok | [5 empty] | 0
ID-S01AP1030-00592 | 592 |  | P33EH1211_HSH | elec.heater EH1211 wet FG clean. sod.hydr. piping - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 14 | 31 | DO |  |  | C | 12.1.5 | EH1211 wet FG clean. sod.hydr. piping - start/stop |  | EH1211 | P33 | EH | 1211 |  | _ | 10 | HSH | P33EH1211_HSH | ok | [5 empty] | 0
ID-S01AP1030-00593 | 593 |  | P33FI1100 | flow FT1100 wet FG clean. wat. to venturi nozzles |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 4W | 0 | ¸ | 30 | m3/h | 220 Vac / .. | 31 |  |  | 0 | 0 | #N/A |  |  | H |  | FT1100 wet FG clean. wat. to venturi nozzles |  | FT1100 | P33 | FI | 1100 |  |  |  |  | P33FI1100 | ok |  |  |  | 0 | 30 | m3/h
ID-S01AP1030-00594 | 594 |  | P33FI1101 | flow FT1101 recirc. wet FG clean. wat. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 100 | m3/h | 220 Vac / .. | 12 |  | 12.1.7.6 | 7 | 14 | AI |  |  | H | 12.1.7 | FT1101 recirc. wet FG clean. wat. |  | FT1101 | P33 | FI | 1101 |  |  |  |  | P33FI1101 | ok |  |  |  | 0 | 100 | m3/h
ID-S01AP1030-00595 | 595 |  | P33FI1102 | flow FT1102 extract. wet FG clean. wat. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 200 | m3/h | 220 Vac / .. | 12 |  | 12.1.7.6 | 8 | 14 | AI |  |  | H | 12.1.7 | FT1102 extract. wet FG clean. wat. |  | FT1102 | P33 | FI | 1102 |  |  |  |  | P33FI1102 | ok |  |  |  | 0 | 200 | m3/h
ID-S01AP1030-00596 | 596 |  | P33FI1150 | flow FT1150 wet FG clean. sod.hydr. to SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 4W | 0 | ¸ | 10 | m3/h | 220 Vac / .. | 31 |  |  | 0 | 0 | #N/A |  |  | H |  | FT1150 wet FG clean. sod.hydr. to SB1100 |  | FT1150 | P33 | FI | 1150 |  |  |  |  | P33FI1150 | ok |  |  |  | 0 | 10 | m3/h
ID-S01AP1030-00597 | 597 |  | P33FI1152 | flow FT1152 extract. wet FG clean. sod.hydr. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 500 | m3/h | 220 Vac / .. | 12 |  | 12.1.7.6 | 9 | 14 | AI |  |  | H | 12.1.7 | FT1152 extract. wet FG clean. sod.hydr. |  | FT1152 | P33 | FI | 1152 |  |  |  |  | P33FI1152 | ok |  |  |  | 0 | 500 | m3/h
ID-S01AP1030-00598 | 598 |  | P33FI1201 | flow FT1201 wet FG clean. sod.hydr. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 1 | m3/h | 220 Vac / .. | 12 |  | 12.1.7.6 | 10 | 14 | AI |  |  | H | 12.1.7 | FT1201 wet FG clean. sod.hydr. |  | FT1201 | P33 | FI | 1201 |  |  |  |  | P33FI1201 | ok |  |  |  | 0 | 1 | m3/h
ID-S01AP1030-00599 | 599 |  | P33FV1102_ZSL | vlv. FV1102 extract. wet FG clean. wat. - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | 0 | ¸ | 10 | m3/h |  | 12 |  | 12.1.8.7 | 21 | 28 | DI |  |  | C | 12.1.8 | FV1102 extract. wet FG clean. wat. - closed |  | FV1102 | P33 | FV | 1102 |  | _ | 10 | ZSL | P33FV1102_ZSL | ok | [5 empty] | m3/h
ID-S01AP1030-00600 | 600 |  | P33FV1102_ZY | vlv. FV1102 extract. wet FG clean. wat. - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.6.1 | 1 | 7 | AO |  |  | C | 12.1.6 | FV1102 extract. wet FG clean. wat. - req.pos. |  | FV1102 | P33 | FV | 1102 |  | _ | 10 | ZY | P33FV1102_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00601 | 601 |  | P33FV1152_ZSL | vlv. FV1152 extract. wet FG clean. sod.hydr. - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.7 | 22 | 28 | DI |  |  | C | 12.1.8 | FV1152 extract. wet FG clean. sod.hydr. - closed |  | FV1152 | P33 | FV | 1152 |  | _ | 10 | ZSL | P33FV1152_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00602 | 602 |  | P33FV1152_ZY | vlv. FV1152 extract. wet FG clean. sod.hydr. - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.6.1 | 2 | 7 | AO |  |  | C | 12.1.6 | FV1152 extract. wet FG clean. sod.hydr. - req.pos. |  | FV1152 | P33 | FV | 1152 |  | _ | 10 | ZY | P33FV1152_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00603 | 603 |  | P33LSLL1100 | lev. LL LSLL1100 wet FG clean. SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.8.7 | 23 | 28 | DI |  |  | D | 12.1.8 | LL LSLL1100 wet FG clean. SB1100 |  | LL | P33 | LSLL | 1100 |  |  |  |  | P33LSLL1100 | ok | [5 empty] | 0
ID-S01AP1030-00604 | 604 |  | P33LSLL1150 | lev. LL LSLL1150 wet FG clean. TK1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.8.7 | 24 | 28 | DI |  |  | D | 12.1.8 | LL LSLL1150 wet FG clean. TK1150 |  | LL | P33 | LSLL | 1150 |  |  |  |  | P33LSLL1150 | ok | [5 empty] | 0
ID-S01AP1030-00605 | 605 |  | P33LSLL1200 | lev. LL LSLL1200 wet FG clean. TK1200 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.8.7 | 25 | 28 | DI |  |  | D | 12.1.8 | LL LSLL1200 wet FG clean. TK1200 |  | LL | P33 | LSLL | 1200 |  |  |  |  | P33LSLL1200 | ok | [5 empty] | 0
ID-S01AP1030-00606 | 606 |  | P33LI1101 | lev. LT1101 wet FG clean. SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  | 12 |  | 12.1.7.6 | 11 | 14 | AI |  |  | C | 12.1.7 | LT1101 wet FG clean. SB1100 |  | LT1101 | P33 | LI | 1101 |  |  |  |  | P33LI1101 | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00607 | 607 |  | P33LI1151 | lev. LT1151 wet FG clean. TK1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-002 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 100 | % |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | LT1151 wet FG clean. TK1150 |  | LT1151 | P33 | LI | 1151 |  |  |  |  | P33LI1151 | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00608 | 608 |  | P33LI1200 | lev. LT1200 wet FG clean. TK1200 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  | 12 |  | 12.1.7.6 | 12 | 14 | AI |  |  | C | 12.1.7 | LT1200 wet FG clean. TK1200 |  | LT1200 | P33 | LI | 1200 |  |  |  |  | P33LI1200 | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00609 | 609 |  | P33LI1300 | lev. LT1300 wet FG clean. reagen. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  | 12 |  | 12.1.7.6 | 13 | 14 | AI |  |  | C | 12.1.7 | LT1300 wet FG clean. reagen. |  | LT1300 | P33 | LI | 1300 |  |  |  |  | P33LI1300 | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00610 | 610 |  | P33LI1400 | lev. LT1400 wet FG clean. reagen. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  | 12 |  | 12.1.7.6 | 14 | 14 | AI |  |  | C | 12.1.7 | LT1400 wet FG clean. reagen. |  | LT1400 | P33 | LI | 1400 |  |  |  |  | P33LI1400 | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00611 | 611 |  | P33LI1500 | lev. LT1500 wet FG clean. pot.perm. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-002 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  | 12 |  | 12.1.8.3 | 1 | 16 | AI |  |  | C | 12.1.8 | LT1500 wet FG clean. pot.perm. |  | LT1500 | P33 | LI | 1500 |  |  |  |  | P33LI1500 | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00612 | 612 |  | P33LV1101_ZSL | vlv. LV1101 filling wet FG clean. wat. SB1100 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.7 | 26 | 28 | DI |  |  | C | 12.1.8 | LV1101 filling wet FG clean. wat. SB1100 - closed |  | LV1101 | P33 | LV | 1101 |  | _ | 10 | ZSL | P33LV1101_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00613 | 613 |  | P33LV1101_ZY | vlv. LV1101 filling wet FG clean. wat. SB1100 - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.6.1 | 3 | 7 | AO |  |  | C | 12.1.6 | LV1101 filling wet FG clean. wat. SB1100 - req.pos. |  | LV1101 | P33 | LV | 1101 |  | _ | 10 | ZY | P33LV1101_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00614 | 614 |  | P33LV1151_ZSL | vlv. LV1151 filling wet FG clean. sod.hydr. TK1150 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.7 | 27 | 28 | DI |  |  | C | 12.1.8 | LV1151 filling wet FG clean. sod.hydr. TK1150 - closed |  | LV1151 | P33 | LV | 1151 |  | _ | 10 | ZSL | P33LV1151_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00615 | 615 |  | P33LV1151_ZY | vlv. LV1151 filling wet FG clean. sod.hydr. TK1150 - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.6.1 | 4 | 7 | AO |  |  | C | 12.1.6 | LV1151 filling wet FG clean. sod.hydr. TK1150 - req.pos. |  | LV1151 | P33 | LV | 1151 |  | _ | 10 | ZY | P33LV1151_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00616 | 616 |  | P33PDI1100 | diff.press. PDT1100 wet FG clean. venturi |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 400 | mmH20 |  | 12 |  | 12.1.8.3 | 2 | 16 | AI |  |  | C | 12.1.8 | PDT1100 wet FG clean. venturi |  | PDT1100 | P33 | PDI | 1100 |  |  |  |  | P33PDI1100 | ok |  |  |  | 0 | 400 | mmH20
ID-S01AP1030-00617 | 617 |  | P33PDI1101 | diff.press. PDT1101 wet FG clean. SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 400 | mmH20 |  | 12 |  | 12.1.8.3 | 3 | 16 | AI |  |  | C | 12.1.8 | PDT1101 wet FG clean. SB1100 |  | PDT1101 | P33 | PDI | 1101 |  |  |  |  | P33PDI1101 | ok |  |  |  | 0 | 400 | mmH20
ID-S01AP1030-00618 | 618 |  | P33POV1103_ZSH | vlv. POV1103 cooling wet FG clean. wat. SB1100 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.7 | 28 | 28 | DI |  |  | C | 12.1.8 | POV1103 cooling wet FG clean. wat. SB1100 - opened |  | POV1103 | P33 | POV | 1103 |  | _ | 11 | ZSH | P33POV1103_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00619 | 619 |  | P33POV1103_ZSL | vlv. POV1103 cooling wet FG clean. wat. SB1100 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.6 | 3 | 17 | DI |  |  | C | 12.1.8 | POV1103 cooling wet FG clean. wat. SB1100 - closed |  | POV1103 | P33 | POV | 1103 |  | _ | 11 | ZSL | P33POV1103_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00620 | 620 |  | P33POV1103_HSL | vlv. POV1103 cooling wet FG clean. wat. SB1100 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DOS | RELAY - 24 Vac | true | → | active | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | POV1103 cooling wet FG clean. wat. SB1100 - close |  | POV1103 | P33 | POV | 1103 |  | _ | 11 | HSL | P33POV1103_HSL | ok | [5 empty] | 0
ID-S01AP1030-00621 | 621 |  | P33PM1100A_YLRE | pump PM1100A recirc. wet FG clean. wat. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 13 | 27 | DI |  |  | C | 12.1.5 | PM1100A recirc. wet FG clean. wat. - in remote |  | PM1100A | P33 | PM | 1100 | A | _ | 11 | YLRE | P33PM1100A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00622 | 622 |  | P33PM1100A_YLH | pump PM1100A recirc. wet FG clean. wat. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 14 | 27 | DI |  |  | C | 12.1.5 | PM1100A recirc. wet FG clean. wat. - in running |  | PM1100A | P33 | PM | 1100 | A | _ | 11 | YLH | P33PM1100A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00623 | 623 |  | P33PM1100A_YSG | pump PM1100A recirc. wet FG clean. wat. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 15 | 27 | DI |  |  | C | 12.1.5 | PM1100A recirc. wet FG clean. wat. - supply fault |  | PM1100A | P33 | PM | 1100 | A | _ | 11 | YSG | P33PM1100A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00624 | 624 |  | P33PM1100A_HSH | pump PM1100A recirc. wet FG clean. wat. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 15 | 31 | DO |  |  | C | 12.1.5 | PM1100A recirc. wet FG clean. wat. - start/stop |  | PM1100A | P33 | PM | 1100 | A | _ | 11 | HSH | P33PM1100A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00625 | 625 |  | P33PM1100B_YLRE | pump PM1100B recirc. wet FG clean. wat. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 13 | 27 | DI |  |  | C | 12.1.6 | PM1100B recirc. wet FG clean. wat. - in remote |  | PM1100B | P33 | PM | 1100 | B | _ | 11 | YLRE | P33PM1100B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00626 | 626 |  | P33PM1100B_YLH | pump PM1100B recirc. wet FG clean. wat. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 14 | 27 | DI |  |  | C | 12.1.6 | PM1100B recirc. wet FG clean. wat. - in running |  | PM1100B | P33 | PM | 1100 | B | _ | 11 | YLH | P33PM1100B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00627 | 627 |  | P33PM1100B_YSG | pump PM1100B recirc. wet FG clean. wat. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 15 | 27 | DI |  |  | C | 12.1.6 | PM1100B recirc. wet FG clean. wat. - supply fault |  | PM1100B | P33 | PM | 1100 | B | _ | 11 | YSG | P33PM1100B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00628 | 628 |  | P33PM1100B_HSH | pump PM1100B recirc. wet FG clean. wat. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 16 | 31 | DO |  |  | C | 12.1.5 | PM1100B recirc. wet FG clean. wat. - start/stop |  | PM1100B | P33 | PM | 1100 | B | _ | 11 | HSH | P33PM1100B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00629 | 629 |  | P33PM1150A_YLRE | pump PM1150A recirc. wet FG clean. sod.hydr. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 16 | 27 | DI |  |  | C | 12.1.5 | PM1150A recirc. wet FG clean. sod.hydr. - in remote |  | PM1150A | P33 | PM | 1150 | A | _ | 11 | YLRE | P33PM1150A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00630 | 630 |  | P33PM1150A_YLH | pump PM1150A recirc. wet FG clean. sod.hydr. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 17 | 27 | DI |  |  | C | 12.1.5 | PM1150A recirc. wet FG clean. sod.hydr. - in running |  | PM1150A | P33 | PM | 1150 | A | _ | 11 | YLH | P33PM1150A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00631 | 631 |  | P33PM1150A_YSG | pump PM1150A recirc. wet FG clean. sod.hydr. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 18 | 27 | DI |  |  | C | 12.1.5 | PM1150A recirc. wet FG clean. sod.hydr. - supply fault |  | PM1150A | P33 | PM | 1150 | A | _ | 11 | YSG | P33PM1150A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00632 | 632 |  | P33PM1150A_HSH | pump PM1150A recirc. wet FG clean. sod.hydr. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 17 | 31 | DO |  |  | C | 12.1.5 | PM1150A recirc. wet FG clean. sod.hydr. - start/stop |  | PM1150A | P33 | PM | 1150 | A | _ | 11 | HSH | P33PM1150A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00633 | 633 |  | P33PM1150B_YLRE | pump PM1150B recirc. wet FG clean. sod.hydr. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 16 | 27 | DI |  |  | C | 12.1.6 | PM1150B recirc. wet FG clean. sod.hydr. - in remote |  | PM1150B | P33 | PM | 1150 | B | _ | 11 | YLRE | P33PM1150B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00634 | 634 |  | P33PM1150B_YLH | pump PM1150B recirc. wet FG clean. sod.hydr. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 17 | 27 | DI |  |  | C | 12.1.6 | PM1150B recirc. wet FG clean. sod.hydr. - in running |  | PM1150B | P33 | PM | 1150 | B | _ | 11 | YLH | P33PM1150B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00635 | 635 |  | P33PM1150B_YSG | pump PM1150B recirc. wet FG clean. sod.hydr. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 18 | 27 | DI |  |  | C | 12.1.6 | PM1150B recirc. wet FG clean. sod.hydr. - supply fault |  | PM1150B | P33 | PM | 1150 | B | _ | 11 | YSG | P33PM1150B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00636 | 636 |  | P33PM1150B_HSH | pump PM1150B recirc. wet FG clean. sod.hydr. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 18 | 31 | DO |  |  | C | 12.1.5 | PM1150B recirc. wet FG clean. sod.hydr. - start/stop |  | PM1150B | P33 | PM | 1150 | B | _ | 11 | HSH | P33PM1150B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00637 | 637 |  | P33PM1200A_II | pump PM1200A dosag. wet FG clean. reagen. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 12 |  | 12.1.6.2 | 7 | 8 | AI |  |  | H | 12.1.6 | PM1200A dosag. wet FG clean. reagen. - current |  | PM1200A | P33 | PM | 1200 | A | _ | 11 | II | P33PM1200A_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1030-00638 | 638 |  | P33PM1200A_YLRE | pump PM1200A dosag. wet FG clean. sod.hydr. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 19 | 27 | DI |  |  | C | 12.1.5 | PM1200A dosag. wet FG clean. sod.hydr. - in remote |  | PM1200A | P33 | PM | 1200 | A | _ | 11 | YLRE | P33PM1200A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00639 | 639 |  | P33PM1200A_YLH | pump PM1200A dosag. wet FG clean. sod.hydr. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 20 | 27 | DI |  |  | C | 12.1.5 | PM1200A dosag. wet FG clean. sod.hydr. - in running |  | PM1200A | P33 | PM | 1200 | A | _ | 11 | YLH | P33PM1200A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00640 | 640 |  | P33PM1200A_YSG | pump PM1200A dosag. wet FG clean. sod.hydr. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 21 | 27 | DI |  |  | C | 12.1.5 | PM1200A dosag. wet FG clean. sod.hydr. - supply fault |  | PM1200A | P33 | PM | 1200 | A | _ | 11 | YSG | P33PM1200A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00641 | 641 |  | P33PM1200A_HSH | pump PM1200A dosag. wet FG clean. sod.hydr. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 19 | 31 | DO |  |  | C | 12.1.5 | PM1200A dosag. wet FG clean. sod.hydr. - start/stop |  | PM1200A | P33 | PM | 1200 | A | _ | 11 | HSH | P33PM1200A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00642 | 642 |  | P33PM1200A_SY | pump PM1200A dosag. wet FG clean. sod.hydr. - req.speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.7.8 | 1 | 4 | AO |  |  | C | 12.1.7 | PM1200A dosag. wet FG clean. sod.hydr. - req.speed |  | PM1200A | P33 | PM | 1200 | A | _ | 11 | SY | P33PM1200A_SY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00643 | 643 |  | P33PM1200A_JY | pump PM1200A dosag. wet FG clean. sod.hydr. - req.range |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.7.8 | 2 | 4 | AO |  |  | C | 12.1.7 | PM1200A dosag. wet FG clean. sod.hydr. - req.range |  | PM1200A | P33 | PM | 1200 | A | _ | 11 | JY | P33PM1200A_JY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00644 | 644 |  | P33PM1200B_II | pump PM1200B dosag. wet FG clean. reagen. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 12 |  | 12.1.6.2 | 8 | 8 | AI |  |  | H | 12.1.6 | PM1200B dosag. wet FG clean. reagen. - current |  | PM1200B | P33 | PM | 1200 | B | _ | 11 | II | P33PM1200B_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1030-00645 | 645 |  | P33PM1200B_YLRE | pump PM1200B dosag. wet FG clean. sod.hydr. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 19 | 27 | DI |  |  | C | 12.1.6 | PM1200B dosag. wet FG clean. sod.hydr. - in remote |  | PM1200B | P33 | PM | 1200 | B | _ | 11 | YLRE | P33PM1200B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00646 | 646 |  | P33PM1200B_YLH | pump PM1200B dosag. wet FG clean. sod.hydr. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 20 | 27 | DI |  |  | C | 12.1.6 | PM1200B dosag. wet FG clean. sod.hydr. - in running |  | PM1200B | P33 | PM | 1200 | B | _ | 11 | YLH | P33PM1200B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00647 | 647 |  | P33PM1200B_YSG | pump PM1200B dosag. wet FG clean. sod.hydr. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 21 | 27 | DI |  |  | C | 12.1.6 | PM1200B dosag. wet FG clean. sod.hydr. - supply fault |  | PM1200B | P33 | PM | 1200 | B | _ | 11 | YSG | P33PM1200B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00648 | 648 |  | P33PM1200B_HSH | pump PM1200B dosag. wet FG clean. sod.hydr. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 20 | 31 | DO |  |  | C | 12.1.5 | PM1200B dosag. wet FG clean. sod.hydr. - start/stop |  | PM1200B | P33 | PM | 1200 | B | _ | 11 | HSH | P33PM1200B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00649 | 649 |  | P33PM1200B_SY | pump PM1200B dosag. wet FG clean. sod.hydr. - req.speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.7.8 | 3 | 4 | AO |  |  | C | 12.1.7 | PM1200B dosag. wet FG clean. sod.hydr. - req.speed |  | PM1200B | P33 | PM | 1200 | B | _ | 11 | SY | P33PM1200B_SY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00650 | 650 |  | P33PM1200B_JY | pump PM1200B dosag. wet FG clean. sod.hydr. - req.range |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.7.8 | 4 | 4 | AO |  |  | C | 12.1.7 | PM1200B dosag. wet FG clean. sod.hydr. - req.range |  | PM1200B | P33 | PM | 1200 | B | _ | 11 | JY | P33PM1200B_JY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00651 | 651 |  | P33PM1300A_YLRE | pump PM1300A dosag. wet FG clean. reagen. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 22 | 27 | DI |  |  | C | 12.1.5 | PM1300A dosag. wet FG clean. reagen. - in remote |  | PM1300A | P33 | PM | 1300 | A | _ | 11 | YLRE | P33PM1300A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00652 | 652 |  | P33PM1300A_YLH | pump PM1300A dosag. wet FG clean. reagen. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 23 | 27 | DI |  |  | C | 12.1.5 | PM1300A dosag. wet FG clean. reagen. - in running |  | PM1300A | P33 | PM | 1300 | A | _ | 11 | YLH | P33PM1300A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00653 | 653 |  | P33PM1300A_YSG | pump PM1300A dosag. wet FG clean. reagen. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 24 | 27 | DI |  |  | C | 12.1.5 | PM1300A dosag. wet FG clean. reagen. - supply fault |  | PM1300A | P33 | PM | 1300 | A | _ | 11 | YSG | P33PM1300A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00654 | 654 |  | P33PM1300A_HSH | pump PM1300A dosag. wet FG clean. reagen. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 21 | 31 | DO |  |  | C | 12.1.5 | PM1300A dosag. wet FG clean. reagen. - start/stop |  | PM1300A | P33 | PM | 1300 | A | _ | 11 | HSH | P33PM1300A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00655 | 655 |  | P33PM1300A_II | pump PM1300A dosag. wet FG clean. reagen. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 |  |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | PM1300A dosag. wet FG clean. reagen. - current |  | PM1300A | P33 | PM | 1300 | A | _ | 11 | II | P33PM1300A_II | ok | [5 empty] | A
ID-S01AP1030-00656 | 656 |  | P33PM1300B_YLRE | pump PM1300B dosag. wet FG clean. reagen. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 22 | 27 | DI |  |  | C | 12.1.6 | PM1300B dosag. wet FG clean. reagen. - in remote |  | PM1300B | P33 | PM | 1300 | B | _ | 11 | YLRE | P33PM1300B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00657 | 657 |  | P33PM1300B_YLH | pump PM1300B dosag. wet FG clean. reagen. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 23 | 27 | DI |  |  | C | 12.1.6 | PM1300B dosag. wet FG clean. reagen. - in running |  | PM1300B | P33 | PM | 1300 | B | _ | 11 | YLH | P33PM1300B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00658 | 658 |  | P33PM1300B_YSG | pump PM1300B dosag. wet FG clean. reagen. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 24 | 27 | DI |  |  | C | 12.1.6 | PM1300B dosag. wet FG clean. reagen. - supply fault |  | PM1300B | P33 | PM | 1300 | B | _ | 11 | YSG | P33PM1300B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00659 | 659 |  | P33PM1300B_HSH | pump PM1300B dosag. wet FG clean. reagen. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 22 | 31 | DO |  |  | C | 12.1.5 | PM1300B dosag. wet FG clean. reagen. - start/stop |  | PM1300B | P33 | PM | 1300 | B | _ | 11 | HSH | P33PM1300B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00660 | 660 |  | P33PM1300B_II | pump PM1300B dosag. wet FG clean. reagen. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 |  |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | PM1300B dosag. wet FG clean. reagen. - current |  | PM1300B | P33 | PM | 1300 | B | _ | 11 | II | P33PM1300B_II | ok | [5 empty] | A
ID-S01AP1030-00661 | 661 |  | P33PM1400A_YLRE | pump PM1400A dosag. wet FG clean. reagen. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 25 | 27 | DI |  |  | C | 12.1.5 | PM1400A dosag. wet FG clean. reagen. - in remote |  | PM1400A | P33 | PM | 1400 | A | _ | 11 | YLRE | P33PM1400A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00662 | 662 |  | P33PM1400A_YLH | pump PM1400A dosag. wet FG clean. reagen. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.2 | 26 | 27 | DI |  |  | C | 12.1.5 | PM1400A dosag. wet FG clean. reagen. - in running |  | PM1400A | P33 | PM | 1400 | A | _ | 11 | YLH | P33PM1400A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00663 | 663 |  | P33PM1400A_YSG | pump PM1400A dosag. wet FG clean. reagen. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.2 | 27 | 27 | DI |  |  | C | 12.1.5 | PM1400A dosag. wet FG clean. reagen. - supply fault |  | PM1400A | P33 | PM | 1400 | A | _ | 11 | YSG | P33PM1400A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00664 | 664 |  | P33PM1400A_HSH | pump PM1400A dosag. wet FG clean. reagen. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 23 | 31 | DO |  |  | C | 12.1.5 | PM1400A dosag. wet FG clean. reagen. - start/stop |  | PM1400A | P33 | PM | 1400 | A | _ | 11 | HSH | P33PM1400A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00665 | 665 |  | P33PM1400A_II | pump PM1400A dosag. wet FG clean. reagen. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 |  |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | PM1400A dosag. wet FG clean. reagen. - current |  | PM1400A | P33 | PM | 1400 | A | _ | 11 | II | P33PM1400A_II | ok | [5 empty] | A
ID-S01AP1030-00666 | 666 |  | P33PM1400B_YLRE | pump PM1400B dosag. wet FG clean. reagen. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 25 | 27 | DI |  |  | C | 12.1.6 | PM1400B dosag. wet FG clean. reagen. - in remote |  | PM1400B | P33 | PM | 1400 | B | _ | 11 | YLRE | P33PM1400B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00667 | 667 |  | P33PM1400B_YLH | pump PM1400B dosag. wet FG clean. reagen. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.7 | 26 | 27 | DI |  |  | C | 12.1.6 | PM1400B dosag. wet FG clean. reagen. - in running |  | PM1400B | P33 | PM | 1400 | B | _ | 11 | YLH | P33PM1400B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00668 | 668 |  | P33PM1400B_YSG | pump PM1400B dosag. wet FG clean. reagen. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.7 | 27 | 27 | DI |  |  | C | 12.1.6 | PM1400B dosag. wet FG clean. reagen. - supply fault |  | PM1400B | P33 | PM | 1400 | B | _ | 11 | YSG | P33PM1400B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00669 | 669 |  | P33PM1400B_HSH | pump PM1400B dosag. wet FG clean. reagen. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 24 | 31 | DO |  |  | C | 12.1.5 | PM1400B dosag. wet FG clean. reagen. - start/stop |  | PM1400B | P33 | PM | 1400 | B | _ | 11 | HSH | P33PM1400B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00670 | 670 |  | P33PM1400B_II | pump PM1400B dosag. wet FG clean. reagen. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 |  |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | PM1400B dosag. wet FG clean. reagen. - current |  | PM1400B | P33 | PM | 1400 | B | _ | 11 | II | P33PM1400B_II | ok | [5 empty] | A
ID-S01AP1030-00671 | 671 |  | P33PM1400C_YLRE | pump PM1400C dosag. wet FG clean. reagen. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | C | 12.1.6.8 | 1 | 25 | DI |  |  | C | 12.1.6 | PM1400C dosag. wet FG clean. reagen. - in remote |  | PM1400C | P33 | PM | 1400 | C | _ | 11 | YLRE | P33PM1400C_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00672 | 672 |  | P33PM1400C_YLH | pump PM1400C dosag. wet FG clean. reagen. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | C | 12.1.6.8 | 2 | 25 | DI |  |  | C | 12.1.6 | PM1400C dosag. wet FG clean. reagen. - in running |  | PM1400C | P33 | PM | 1400 | C | _ | 11 | YLH | P33PM1400C_YLH | ok | [5 empty] | 0
ID-S01AP1030-00673 | 673 |  | P33PM1400C_YSG | pump PM1400C dosag. wet FG clean. reagen. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | C | 12.1.6.8 | 3 | 25 | DI |  |  | C | 12.1.6 | PM1400C dosag. wet FG clean. reagen. - supply fault |  | PM1400C | P33 | PM | 1400 | C | _ | 11 | YSG | P33PM1400C_YSG | ok | [5 empty] | 0
ID-S01AP1030-00674 | 674 |  | P33PM1400C_HSH | pump PM1400C dosag. wet FG clean. reagen. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 25 | 31 | DO |  |  | C | 12.1.5 | PM1400C dosag. wet FG clean. reagen. - start/stop |  | PM1400C | P33 | PM | 1400 | C | _ | 11 | HSH | P33PM1400C_HSH | ok | [5 empty] | 0
ID-S01AP1030-00675 | 675 |  | P33PM1400C_II | pump PM1400C dosag. wet FG clean. reagen. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 |  |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | PM1400C dosag. wet FG clean. reagen. - current |  | PM1400C | P33 | PM | 1400 | C | _ | 11 | II | P33PM1400C_II | ok | [5 empty] | A
ID-S01AP1030-00676 | 676 |  | P33PM1500A_YLRE | pump PM1500A dosag. wet FG clean. pot.perm. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.1 | 26 | 28 | DI |  |  | C | 12.1.5 | PM1500A dosag. wet FG clean. pot.perm. - in remote |  | PM1500A | P33 | PM | 1500 | A | _ | 11 | YLRE | P33PM1500A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00677 | 677 |  | P33PM1500A_YLH | pump PM1500A dosag. wet FG clean. pot.perm. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.5.1 | 27 | 28 | DI |  |  | C | 12.1.5 | PM1500A dosag. wet FG clean. pot.perm. - in running |  | PM1500A | P33 | PM | 1500 | A | _ | 11 | YLH | P33PM1500A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00678 | 678 |  | P33PM1500A_YSG | pump PM1500A dosag. wet FG clean. pot.perm. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.5.1 | 28 | 28 | DI |  |  | C | 12.1.5 | PM1500A dosag. wet FG clean. pot.perm. - supply fault |  | PM1500A | P33 | PM | 1500 | A | _ | 11 | YSG | P33PM1500A_YSG | ok | [5 empty] | 0
ID-S01AP1030-00679 | 679 |  | P33PM1500A_HSH | pump PM1500A dosag. wet FG clean. pot.perm. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 26 | 31 | DO |  |  | C | 12.1.5 | PM1500A dosag. wet FG clean. pot.perm. - start/stop |  | PM1500A | P33 | PM | 1500 | A | _ | 11 | HSH | P33PM1500A_HSH | ok | [5 empty] | 0
ID-S01AP1030-00680 | 680 |  | P33PM1500A_II | pump PM1500A dosag. wet FG clean. pot.perm. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 |  |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | PM1500A dosag. wet FG clean. pot.perm. - current |  | PM1500A | P33 | PM | 1500 | A | _ | 11 | II | P33PM1500A_II | ok | [5 empty] | A
ID-S01AP1030-00681 | 681 |  | P33PM1500B_YLRE | pump PM1500B dosag. wet FG clean. pot.perm. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.6 | 22 | 24 | DI |  |  | C | 12.1.6 | PM1500B dosag. wet FG clean. pot.perm. - in remote |  | PM1500B | P33 | PM | 1500 | B | _ | 11 | YLRE | P33PM1500B_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00682 | 682 |  | P33PM1500B_YLH | pump PM1500B dosag. wet FG clean. pot.perm. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.6.6 | 23 | 24 | DI |  |  | C | 12.1.6 | PM1500B dosag. wet FG clean. pot.perm. - in running |  | PM1500B | P33 | PM | 1500 | B | _ | 11 | YLH | P33PM1500B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00683 | 683 |  | P33PM1500B_YSG | pump PM1500B dosag. wet FG clean. pot.perm. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.6.6 | 24 | 24 | DI |  |  | C | 12.1.6 | PM1500B dosag. wet FG clean. pot.perm. - supply fault |  | PM1500B | P33 | PM | 1500 | B | _ | 11 | YSG | P33PM1500B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00684 | 684 |  | P33PM1500B_HSH | pump PM1500B dosag. wet FG clean. pot.perm. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.5.4 | 27 | 31 | DO |  |  | C | 12.1.5 | PM1500B dosag. wet FG clean. pot.perm. - start/stop |  | PM1500B | P33 | PM | 1500 | B | _ | 11 | HSH | P33PM1500B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00685 | 685 |  | P33PM1500B_II | pump PM1500B dosag. wet FG clean. pot.perm. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 |  |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | PM1500B dosag. wet FG clean. pot.perm. - current |  | PM1500B | P33 | PM | 1500 | B | _ | 11 | II | P33PM1500B_II | ok | [5 empty] | A
ID-S01AP1030-00686 | 686 |  | P33PSL1101 | pres. L PSL1101 filling wet FG clean. wat. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.6 | 4 | 17 | DI |  |  | C | 12.1.8 | L PSL1101 filling wet FG clean. wat. |  | L | P33 | PSL | 1101 |  |  |  |  | P33PSL1101 | ok | [5 empty] | 0
ID-S01AP1030-00687 | 687 |  | P33PSL1103 | pres. L PSL1103 cooling wet FG clean. wat. SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.6 | 5 | 17 | DI |  |  | C | 12.1.8 | L PSL1103 cooling wet FG clean. wat. SB1100 |  | L | P33 | PSL | 1103 |  |  |  |  | P33PSL1103 | ok | [5 empty] | 0
ID-S01AP1030-00688 | 688 |  | P33EH1410_YLH | elec.heater EH1410 - Insolub. TMT stor. tank - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active |  |  | 12 |  | 12.1.6.8 | 4 | 25 | DI |  |  | A | 12.1.6 | EH1410 - Insolub. TMT stor. tank - in running |  | EH1410 | P33 | EH | 1410 |  | _ | 10 | YLH | P33EH1410_YLH | ok
ID-S01AP1030-00689 | 689 |  | P33EH1410_YSG | elec.heater EH1410 - Insolub. TMT stor. tank - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active |  |  | 12 |  | 12.1.6.8 | 5 | 25 | DI |  |  | A | 12.1.6 | EH1410 - Insolub. TMT stor. tank - supply fault |  | EH1410 | P33 | EH | 1410 |  | _ | 10 | YSG | P33EH1410_YSG | ok
ID-S01AP1030-00690 | 690 |  | P33EH1410_HSH | elec.heater EH1410 - Insolub. TMT stor. tank - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start |  |  | 12 |  | 12.1.5.4 | 28 | 31 | DO |  |  | A | 12.1.5 | EH1410 - Insolub. TMT stor. tank - start/stop |  | EH1410 | P33 | EH | 1410 |  | _ | 10 | HSH | P33EH1410_HSH | ok
ID-S01AP1030-00691 | 691 |  | P33EH1411_YLH | elec.heater EH1411 - RE012 line - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active |  |  | 12 |  | 12.1.6.8 | 6 | 25 | DI |  |  | A | 12.1.6 | EH1411 - RE012 line - in running |  | EH1411 | P33 | EH | 1411 |  | _ | 10 | YLH | P33EH1411_YLH | ok
ID-S01AP1030-00692 | 692 |  | P33EH1411_YSG | elec.heater EH1411 - RE012 line - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active |  |  | 12 |  | 12.1.6.8 | 7 | 25 | DI |  |  | A | 12.1.6 | EH1411 - RE012 line - supply fault |  | EH1411 | P33 | EH | 1411 |  | _ | 10 | YSG | P33EH1411_YSG | ok
ID-S01AP1030-00693 | 693 |  | P33EH1411_HSH | elec.heater EH1411 - RE012 line - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start |  |  | 12 |  | 12.1.5.4 | 29 | 31 | DO |  |  | A | 12.1.5 | EH1411 - RE012 line - start/stop |  | EH1411 | P33 | EH | 1411 |  | _ | 10 | HSH | P33EH1411_HSH | ok
ID-S01AP1030-00694 | 694 |  | P33EH1510_YLH | elec.heater EH1510 - Potass. Permang. stor. tank - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active |  |  | 12 |  | 12.1.6.8 | 8 | 25 | DI |  |  | A | 12.1.6 | EH1510 - Potass. Permang. stor. tank - in running |  | EH1510 | P33 | EH | 1510 |  | _ | 10 | YLH | P33EH1510_YLH | ok
ID-S01AP1030-00695 | 695 |  | P33EH1510_YSG | elec.heater EH1510 - Potass. Permang. stor. tank - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active |  |  | 12 |  | 12.1.6.8 | 9 | 25 | DI |  |  | A | 12.1.6 | EH1510 - Potass. Permang. stor. tank - supply fault |  | EH1510 | P33 | EH | 1510 |  | _ | 10 | YSG | P33EH1510_YSG | ok
ID-S01AP1030-00696 | 696 |  | P33EH1510_HSH | elec.heater EH1510 - Potass. Permang. stor. tank - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start |  |  | 12 |  | 12.1.5.4 | 30 | 31 | DO |  |  | A | 12.1.5 | EH1510 - Potass. Permang. stor. tank - start/stop |  | EH1510 | P33 | EH | 1510 |  | _ | 10 | HSH | P33EH1510_HSH | ok
ID-S01AP1030-00697 | 697 |  | P33EH1511_YLH | elec.heater EH1511 - RE001 line - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active |  |  | 12 |  | 12.1.6.8 | 10 | 25 | DI |  |  | A | 12.1.6 | EH1511 - RE001 line - in running |  | EH1511 | P33 | EH | 1511 |  | _ | 10 | YLH | P33EH1511_YLH | ok
ID-S01AP1030-00698 | 698 |  | P33EH1511_YSG | elec.heater EH1511 - RE001 line - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active |  |  | 12 |  | 12.1.6.8 | 11 | 25 | DI |  |  | A | 12.1.6 | EH1511 - RE001 line - supply fault |  | EH1511 | P33 | EH | 1511 |  | _ | 10 | YSG | P33EH1511_YSG | ok
ID-S01AP1030-00699 | 699 |  | P33EH1511_HSH | elec.heater EH1511 - RE001 line - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | P33MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start |  |  | 12 |  | 12.1.5.4 | 31 | 31 | DO |  |  | A | 12.1.5 | EH1511 - RE001 line - start/stop |  | EH1511 | P33 | EH | 1511 |  | _ | 10 | HSH | P33EH1511_HSH | ok
ID-S01AP1030-00700 | 700 |  | P33TSH1210 | temp. H TSH1210 wet FG clean. TK1200 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.6 | 6 | 17 | DI |  |  | C | 12.1.8 | H TSH1210 wet FG clean. TK1200 |  | H | P33 | TSH | 1210 |  |  |  |  | P33TSH1210 | ok | [5 empty] | 0
ID-S01AP1030-00701 | 701 |  | P33TI1100A | temp. TT1100A wet FG clean. inlet SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1100A wet FG clean. inlet SB1100 |  | TT1100A | P33 | TI | 1100 | A |  |  |  | P33TI1100A | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00702 | 702 |  | P33TI1100B | temp. TT1100B wet FG clean. inlet SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1100B wet FG clean. inlet SB1100 |  | TT1100B | P33 | TI | 1100 | B |  |  |  | P33TI1100B | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00703 | 703 |  | P33TI1100C | temp. TT1100C wet FG clean. SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.8.3 | 4 | 16 | AI |  |  | C | 12.1.8 | TT1100C wet FG clean. SB1100 |  | TT1100C | P33 | TI | 1100 | C |  |  |  | P33TI1100C | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00704 | 704 |  | P33TI1101 | temp. TT1101 recirc. wet FG clean. wat. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP01 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | °C |  | 12 |  | 12.1.8.3 | 5 | 16 | AI |  |  | C | 12.1.8 | TT1101 recirc. wet FG clean. wat. |  | TT1101 | P33 | TI | 1101 |  |  |  |  | P33TI1101 | ok |  |  |  | 0 | 100 | °C
ID-S01AP1030-00705 | 705 |  | P33TI1151 | temp. TT1151 wet FG clean. sod.hydr. to HE1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | °C |  | 12 |  | 12.1.8.3 | 6 | 16 | AI |  |  | C | 12.1.8 | TT1151 wet FG clean. sod.hydr. to HE1150 |  | TT1151 | P33 | TI | 1151 |  |  |  |  | P33TI1151 | ok |  |  |  | 0 | 100 | °C
ID-S01AP1030-00706 | 706 |  | P33TI1152 | temp. TT1152 wet FG clean. sod.hydr. to SB1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P33 DP02 | CHN1-TDZ2-P33-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | °C |  | 12 |  | 12.1.8.3 | 7 | 16 | AI |  |  | C | 12.1.8 | TT1152 wet FG clean. sod.hydr. to SB1100 |  | TT1152 | P33 | TI | 1152 |  |  |  |  | P33TI1152 | ok |  |  |  | 0 | 100 | °C
ID-S01AP1030-00707 | 707 |  | P35FN1101_YLRE | fan FN1101 f.gas extr. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.4.8 | 16 | 26 | DI |  |  | C | 12.1.4 | FN1101 f.gas extr. - in remote |  | FN1101 | P35 | FN | 1101 |  | _ | 10 | YLRE | P35FN1101_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00708 | 708 |  | P35FN1101_YLH | fan FN1101 f.gas extr. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.4.8 | 17 | 26 | DI |  |  | C | 12.1.4 | FN1101 f.gas extr. - in running |  | FN1101 | P35 | FN | 1101 |  | _ | 10 | YLH | P35FN1101_YLH | ok | [5 empty] | 0
ID-S01AP1030-00709 | 709 |  | P35FN1101_YS | fan FN1101 f.gas extr. - gen.fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.4.8 | 18 | 26 | DI |  |  | C | 12.1.4 | FN1101 f.gas extr. - gen.fault |  | FN1101 | P35 | FN | 1101 |  | _ | 10 | YS | P35FN1101_YS | ok | [5 empty] | 0
ID-S01AP1030-00710 | 710 |  | P35FN1101_YSG | fan FN1101 f.gas extr. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.4.8 | 19 | 26 | DI |  |  | C | 12.1.4 | FN1101 f.gas extr. - supply fault |  | FN1101 | P35 | FN | 1101 |  | _ | 10 | YSG | P35FN1101_YSG | ok | [5 empty] | 0
ID-S01AP1030-00711 | 711 |  | P35FN1101_HSH | fan FN1101 f.gas extr. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 3 | 24 | DO |  |  | C | 12.1.3 | FN1101 f.gas extr. - start/stop |  | FN1101 | P35 | FN | 1101 |  | _ | 10 | HSH | P35FN1101_HSH | ok | [5 empty] | 0
ID-S01AP1030-00712 | 712 |  | P35FN1101_HSK | fan FN1101 f.gas extr. - interlock |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DOS | RELAY | false | → | interlock | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | FN1101 f.gas extr. - interlock |  | FN1101 | P35 | FN | 1101 |  | _ | 10 | HSK | P35FN1101_HSK | ok | [5 empty] | 0
ID-S01AP1030-00713 | 713 |  | P35FN1101_SI | fan FN1101 f.gas extr. - speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.7 | 13 | 14 | AI |  |  | H | 12.1.1 | FN1101 f.gas extr. - speed |  | FN1101 | P35 | FN | 1101 |  | _ | 10 | SI | P35FN1101_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00714 | 714 |  | P35FN1101_II | fan FN1101 f.gas extr. - current |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 12 |  | 12.1.1.7 | 14 | 14 | AI |  |  | H | 12.1.1 | FN1101 f.gas extr. - current |  | FN1101 | P35 | FN | 1101 |  | _ | 10 | II | P35FN1101_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1030-00715 | 715 |  | P35FN1101_SY | fan FN1101 f.gas extr. - req.speed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.1.8 | 8 | 8 | AO |  |  | C | 12.1.1 | FN1101 f.gas extr. - req.speed |  | FN1101 | P35 | FN | 1101 |  | _ | 10 | SY | P35FN1101_SY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00716 | 716 |  | P35FN1101_ST | speed ST1101 f.gas extr. FN1101 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35 LP1101 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | RPM |  | 12 |  | 12.1.6.1 | 5 | 7 | AO |  |  | E | 12.1.6 | ST1101 f.gas extr. FN1101 |  | ST1101 | P35 | FN | 1101 |  | _ | 10 | ST | P35FN1101_ST | ok |  |  |  | 0 |  | RPM
ID-S01AP1030-00717 | 717 |  | P35LI1202 | lev. LT1202 f.gas extr. moist PRV1200 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 100 | % |  | 12 |  | 12.1.8.3 | 8 | 16 | AI |  |  | C | 12.1.8 | LT1202 f.gas extr. moist PRV1200 |  | LT1202 | P35 | LI | 1202 |  |  |  |  | P35LI1202 | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00718 | 718 |  | P35LV1202_ZSL | vlv. LV1202 f.gas extr. moist outlet PRV1200 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.6 | 7 | 17 | DI |  |  | C | 12.1.8 | LV1202 f.gas extr. moist outlet PRV1200 - closed |  | LV1202 | P35 | LV | 1202 |  | _ | 10 | ZSL | P35LV1202_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00719 | 719 |  | P35LV1202_ZY | vlv. LV1202 f.gas extr. moist outlet PRV1200 - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.6.1 | 6 | 7 | AO |  |  | C | 12.1.6 | LV1202 f.gas extr. moist outlet PRV1200 - req.pos. |  | LV1202 | P35 | LV | 1202 |  | _ | 10 | ZY | P35LV1202_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00720 | 720 |  | P35PDI1100 | diff.press. PDT1100 f.gas extr. EH1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 200 | mmH20 |  | 12 |  | 12.1.8.3 | 9 | 16 | AI |  |  | C | 12.1.8 | PDT1100 f.gas extr. EH1100 |  | PDT1100 | P35 | PDI | 1100 |  |  |  |  | P35PDI1100 | ok |  |  |  | 0 | 200 | mmH20
ID-S01AP1030-00721 | 721 |  | P35EM1101B_YLH | elec.mot. EM1101B f.gas extr. emergency - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | B | 12.1.4.8 | 20 | 26 | DI |  |  | C | 12.1.4 | EM1101B f.gas extr. emergency - in running |  | EM1101B | P35 | EM | 1101 | B | _ | 11 | YLH | P35EM1101B_YLH | ok | [5 empty] | 0
ID-S01AP1030-00722 | 722 |  | P35EM1101B_YSG | elec.mot. EM1101B f.gas extr. emergency - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | B | 12.1.4.8 | 21 | 26 | DI |  |  | C | 12.1.4 | EM1101B f.gas extr. emergency - supply fault |  | EM1101B | P35 | EM | 1101 | B | _ | 11 | YSG | P35EM1101B_YSG | ok | [5 empty] | 0
ID-S01AP1030-00723 | 723 |  | P35EM1101B_HSH | elec.mot. EM1101B f.gas extr. emergency - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 4 | 24 | DO |  |  | C | 12.1.3 | EM1101B f.gas extr. emergency - start/stop |  | EM1101B | P35 | EM | 1101 | B | _ | 11 | HSH | P35EM1101B_HSH | ok | [5 empty] | 0
ID-S01AP1030-00724 | 724 |  | P35EM1101B_HSK | elec.mot. EM1101B f.gas extr. emergency - interlock |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35MCC1001 |  | S01AP1030 |  |  |  |  | DOS | RELAY | false | → | interlock | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | EM1101B f.gas extr. emergency - interlock |  | EM1101B | P35 | EM | 1101 | B | _ | 11 | HSK | P35EM1101B_HSK | ok | [5 empty] | 0
ID-S01AP1030-00725 | 725 |  | P35EH1110_YLH | elec.heater EH1110 f.gas extr. EM1101B - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.4.8 | 22 | 26 | DI |  |  | C | 12.1.4 | EH1110 f.gas extr. EM1101B - in running |  | EH1110 | P35 | EH | 1110 |  | _ | 10 | YLH | P35EH1110_YLH | ok | [5 empty] | 0
ID-S01AP1030-00726 | 726 |  | P35EH1110_YSG | elec.heater EH1110 f.gas extr. EM1101B - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.4.8 | 23 | 26 | DI |  |  | C | 12.1.4 | EH1110 f.gas extr. EM1101B - supply fault |  | EH1110 | P35 | EH | 1110 |  | _ | 10 | YSG | P35EH1110_YSG | ok | [5 empty] | 0
ID-S01AP1030-00727 | 727 |  | P35EH1110_HSH | elec.heater EH1110 f.gas extr. EM1101B - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 5 | 24 | DO |  |  | C | 12.1.3 | EH1110 f.gas extr. EM1101B - start/stop |  | EH1110 | P35 | EH | 1110 |  | _ | 10 | HSH | P35EH1110_HSH | ok | [5 empty] | 0
ID-S01AP1030-00728 | 728 |  | P35FN1120_YLH | fan FN1120 cooling f.gas extr. acustic cabin - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.4.8 | 24 | 26 | DI |  |  | C | 12.1.4 | FN1120 cooling f.gas extr. acustic cabin - in running |  | FN1120 | P35 | FN | 1120 |  | _ | 10 | YLH | P35FN1120_YLH | ok | [5 empty] | 0
ID-S01AP1030-00729 | 729 |  | P35FN1120_YSG | fan FN1120 cooling f.gas extr. acustic cabin - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.4.8 | 25 | 26 | DI |  |  | C | 12.1.4 | FN1120 cooling f.gas extr. acustic cabin - supply fault |  | FN1120 | P35 | FN | 1120 |  | _ | 10 | YSG | P35FN1120_YSG | ok | [5 empty] | 0
ID-S01AP1030-00730 | 730 |  | P35FN1120_HSH | fan FN1120 cooling f.gas extr. acustic cabin - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | P35INV1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 6 | 24 | DO |  |  | C | 12.1.3 | FN1120 cooling f.gas extr. acustic cabin - start/stop |  | FN1120 | P35 | FN | 1120 |  | _ | 10 | HSH | P35FN1120_HSH | ok | [5 empty] | 0
ID-S01AP1030-00731 | 731 |  | P35PI1101X | press. PT1101X f.gas extr. inlet FN1101 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | -1500 | ¸ | 0 | mmH20 |  | 12 |  | 12.1.8.3 | 10 | 16 | AI |  |  | C | 12.1.8 | PT1101X f.gas extr. inlet FN1101 |  | PT1101X | P35 | PI | 1101 | X |  |  |  | P35PI1101X | ok |  |  |  | -1500 | 0 | mmH20
ID-S01AP1030-00732 | 732 |  | P35PI1101Y | press. PT1101Y f.gas extr. inlet FN1101 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | -1500 | ¸ | 0 | mmH20 |  | 12 |  | 12.1.8.3 | 11 | 16 | AI |  |  | C | 12.1.8 | PT1101Y f.gas extr. inlet FN1101 |  | PT1101Y | P35 | PI | 1101 | Y |  |  |  | P35PI1101Y | ok |  |  |  | -1500 | 0 | mmH20
ID-S01AP1030-00733 | 733 |  | P35TSH1120 | temp. H TSH1120 f.gas extr. Acoustic cabin |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.6 | 8 | 17 | DI | Switches contained on the same instrument |  | C | 12.1.8 | H TSH1120 f.gas extr. Acoustic cabin |  | H | P35 | TSH | 1120 |  |  |  |  | P35TSH1120 | ok | [5 empty] | 0
ID-S01AP1030-00734 | 734 |  | P35TSHH1120 | temp. HH TSHH1120 f.gas extr. Acoustic cabin |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.8.6 | 9 | 17 | DI |  |  | C | 12.1.8 | HH TSHH1120 f.gas extr. Acoustic cabin |  | HH | P35 | TSHH | 1120 |  |  |  |  | P35TSHH1120 | ok | [5 empty] | 0
ID-S01AP1030-00735 | 735 |  | P35TI1100 | temp. TT1100 f.gas extr. inlet HE1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.8.3 | 12 | 16 | AI |  |  | C | 12.1.8 | TT1100 f.gas extr. inlet HE1100 |  | TT1100 | P35 | TI | 1100 |  |  |  |  | P35TI1100 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00736 | 736 |  | P35TI1101X | temp. TT1101X f.gas extr. FN1101 bearings |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1101X f.gas extr. FN1101 bearings |  | TT1101X | P35 | TI | 1101 | X |  |  |  | P35TI1101X | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00737 | 737 |  | P35TI1101Y | temp. TT1101Y f.gas extr. FN1101 bearings |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1101Y f.gas extr. FN1101 bearings |  | TT1101Y | P35 | TI | 1101 | Y |  |  |  | P35TI1101Y | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00738 | 738 |  | P35TI1102X | temp. TT1102X f.gas extr. FN1101 motor phase |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | M1101A |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1102X f.gas extr. FN1101 motor phase |  | TT1102X | P35 | TI | 1102 | X |  |  |  | P35TI1102X | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00739 | 739 |  | P35TI1102Y | temp. TT1102Y f.gas extr. FN1101 motor phase |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | M1101A |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1102Y f.gas extr. FN1101 motor phase |  | TT1102Y | P35 | TI | 1102 | Y |  |  |  | P35TI1102Y | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00740 | 740 |  | P35TI1102Z | temp. TT1102Z f.gas extr. FN1101 motor phase |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | M1101A |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1102Z f.gas extr. FN1101 motor phase |  | TT1102Z | P35 | TI | 1102 | Z |  |  |  | P35TI1102Z | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00741 | 741 |  | P35TI1103X | temp. TT1103X f.gas extr. FN1101 motor bear. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | M1101A |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1103X f.gas extr. FN1101 motor bear. |  | TT1103X | P35 | TI | 1103 | X |  |  |  | P35TI1103X | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00742 | 742 |  | P35TI1103Y | temp. TT1103Y f.gas extr. FN1101 motor bear. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | M1101A |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 200 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | TT1103Y f.gas extr. FN1101 motor bear. |  | TT1103Y | P35 | TI | 1103 | Y |  |  |  | P35TI1103Y | ok |  |  |  | 0 | 200 | °C
ID-S01AP1030-00743 | 743 |  | P35TI1104 | temp. TT1104 f.gas extr. inlet FN1101 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 300 | °C |  | 12 |  | 12.1.8.3 | 13 | 16 | AI |  |  | C | 12.1.8 | TT1104 f.gas extr. inlet FN1101 |  | TT1104 | P35 | TI | 1104 |  |  |  |  | P35TI1104 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1030-00744 | 744 |  | P35TI1201 | temp. TT1201 f.gas extr. moist PRV1200 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ¸ | 450 | °C |  | 12 |  | 12.1.8.3 | 14 | 16 | AI |  |  | C | 12.1.8 | TT1201 f.gas extr. moist PRV1200 |  | TT1201 | P35 | TI | 1201 |  |  |  |  | P35TI1201 | ok |  |  |  | 0 | 450 | °C
ID-S01AP1030-00745 | 745 |  | P35TV1200_ZSL | vlv. TV1200 f.gas extr. steam inlet HE1100 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.6 | 10 | 17 | DI |  |  | C | 12.1.8 | TV1200 f.gas extr. steam inlet HE1100 - closed |  | TV1200 | P35 | TV | 1200 |  | _ | 10 | ZSL | P35TV1200_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00746 | 746 |  | P35TV1200_ZY | vlv. TV1200 f.gas extr. steam inlet HE1100 - req.pos. |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 12 |  | 12.1.6.1 | 7 | 7 | AO |  |  | C | 12.1.6 | TV1200 f.gas extr. steam inlet HE1100 - req.pos. |  | TV1200 | P35 | TV | 1200 |  | _ | 10 | ZY | P35TV1200_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1030-00747 | 747 |  | P35VI1101X | vibr. VT1101X f.gas extr. FN1101 bearings |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 20 | mm/s |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | VT1101X f.gas extr. FN1101 bearings |  | VT1101X | P35 | VI | 1101 | X |  |  |  | P35VI1101X | ok |  |  |  | 0 | 20 | mm/s
ID-S01AP1030-00748 | 748 |  | P35VI1101Y | vibr. VT1101Y f.gas extr. FN1101 bearings |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P35 DP01 | CHN1-TDZ2-P35-JBA-1-001 |  | S01AP1030 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ¸ | 20 | mm/s |  | 31 |  |  | 0 | 0 | #N/A |  |  | G |  | VT1101Y f.gas extr. FN1101 bearings |  | VT1101Y | P35 | VI | 1101 | Y |  |  |  | P35VI1101Y | ok |  |  |  | 0 | 20 | mm/s
ID-S01AP1030-00749 | 749 |  | P82CD1350_YLRE | aut.pan. AP1350 cleaning dust FF1150 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.4.8 | 26 | 26 | DI |  |  | C | 12.1.4 | AP1350 cleaning dust FF1150 - in remote |  | AP1350 | P82 | CD | 1350 |  | _ | 10 | YLRE | P82CD1350_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00750 | 750 |  | P82CD1350_YSA | aut.pan. AP1350 cleaning dust FF1150 - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.4.6 | 1 | 6 | DI |  |  | C | 12.1.4 | AP1350 cleaning dust FF1150 - com.alarm |  | AP1350 | P82 | CD | 1350 |  | _ | 10 | YSA | P82CD1350_YSA | ok | [5 empty] | 0
ID-S01AP1030-00751 | 751 |  | P82CD1350_HSH | aut.pan. AP1350 cleaning dust FF1150 - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 12 |  | 12.1.4.5 | 28 | 31 | DO |  |  | C | 12.1.4 | AP1350 cleaning dust FF1150 - enable |  | AP1350 | P82 | CD | 1350 |  | _ | 10 | HSH | P82CD1350_HSH | ok | [5 empty] | 0
ID-S01AP1030-00752 | 752 |  | P82BAC1153A_YLRE | bin activ. BAC1153A dust silos SL1150 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.3.1 | 27 | 29 | DI |  |  | C | 12.1.3 | activ. BAC1153A dust silos SL1150 - in remote |  | activ. | P82 | BAC | 1153 | A | _ | 12 | YLRE | P82BAC1153A_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00753 | 753 |  | P82BAC1153A_YLH | bin activ. BAC1153A dust silos SL1150 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 | A | 12.1.3.1 | 28 | 29 | DI |  |  | C | 12.1.3 | activ. BAC1153A dust silos SL1150 - in running |  | activ. | P82 | BAC | 1153 | A | _ | 12 | YLH | P82BAC1153A_YLH | ok | [5 empty] | 0
ID-S01AP1030-00754 | 754 |  | P82BAC1153A_YSG | bin activ. BAC1153A dust silos SL1150 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 | A | 12.1.3.1 | 29 | 29 | DI |  |  | C | 12.1.3 | activ. BAC1153A dust silos SL1150 - supply fault |  | activ. | P82 | BAC | 1153 | A | _ | 12 | YSG | P82BAC1153A_YSG | ok | elec.heater EH1222 FG quenc. wat. to nebul 1 |  |  |  |  | 0
ID-S01AP1030-00755 | 755 |  | P82BAC1153A_HSH | bin activ. BAC1153A dust silos SL1150 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 7 | 24 | DO |  |  | C | 12.1.3 | activ. BAC1153A dust silos SL1150 - start/stop |  | activ. | P82 | BAC | 1153 | A | _ | 12 | HSH | P82BAC1153A_HSH | ok | elec.heater EH1223 FG quenc. wat. to nebul 2 |  |  |  |  | 0
ID-S01AP1030-00756 | 756 |  | P82CAP1156_ZSL | cmd.aut.pan. CAP1156 extract. dust SL1100 - on truck |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | attivo | 0 |  | 12 |  | 12.1.4.6 | 2 | 6 | DI |  |  | C | 12.1.4 | CAP1156 extract. dust SL1100 - on truck |  | CAP1156 | P82 | CAP | 1156 |  | _ | 11 | ZSL | P82CAP1156_ZSL | ok | elec.heater EH1224 FG quenc. wat. to nebul 3 |  |  |  |  | 0
ID-S01AP1030-00757 | 757 |  | P82CAP1156_ZSH | cmd.aut.pan. CAP1156 extract. dust SL1100 - high position |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | attivo | 0 |  | 12 |  | 12.1.4.6 | 3 | 6 | DI |  |  | C | 12.1.4 | CAP1156 extract. dust SL1100 - high position |  | CAP1156 | P82 | CAP | 1156 |  | _ | 11 | ZSH | P82CAP1156_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00758 | 758 |  | P82CAP1156_YLH | cmd.aut.pan. CAP1156 extract. dust SL1100 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | in marcia | 0 |  | 12 |  | 12.1.4.6 | 4 | 6 | DI |  |  | C | 12.1.4 | CAP1156 extract. dust SL1100 - in running |  | CAP1156 | P82 | CAP | 1156 |  | _ | 11 | YLH | P82CAP1156_YLH | ok | [5 empty] | 0
ID-S01AP1030-00759 | 759 |  | P82CAP1156_YLL | cmd.aut.pan. CAP1156 extract. dust SL1100 - stopped |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | fermo | 0 |  | 12 |  | 12.1.4.6 | 5 | 6 | DI |  |  | C | 12.1.4 | CAP1156 extract. dust SL1100 - stopped |  | CAP1156 | P82 | CAP | 1156 |  | _ | 11 | YLL | P82CAP1156_YLL | ok | [5 empty] | 0
ID-S01AP1030-00760 | 760 |  | P82CAP1156_YSA | cmd.aut.pan. CAP1156 extract. dust SL1100 - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | allarme | 0 |  | 12 |  | 12.1.4.6 | 6 | 6 | DI |  |  | C | 12.1.4 | CAP1156 extract. dust SL1100 - com.alarm |  | CAP1156 | P82 | CAP | 1156 |  | _ | 11 | YSA | P82CAP1156_YSA | ok | [5 empty] | 0
ID-S01AP1030-00761 | 761 |  | P82CAP1156_HSH | cmd.aut.pan. CAP1156 extract. dust SL1100 - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | abilitaz. | 0 |  | 12 |  | 12.1.4.5 | 29 | 31 | DO |  |  | C | 12.1.4 | CAP1156 extract. dust SL1100 - enable |  | CAP1156 | P82 | CAP | 1156 |  | _ | 11 | HSH | P82CAP1156_HSH | ok | [5 empty] | 0
ID-S01AP1030-00762 | 762 |  | P82CAP1156_ZAH | cmd.aut.pan. CAP1156 extract. dust SL1100 - POV155 open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 30 | 31 | DO |  |  | C | 12.1.4 | CAP1156 extract. dust SL1100 - POV155 open |  | CAP1156 | P82 | CAP | 1156 |  | _ | 11 | ZAH | P82CAP1156_ZAH | ok | [5 empty] | 0
ID-S01AP1030-00763 | 763 |  | P82CAP1156_ZAL | cmd.aut.pan. CAP1156 extract. dust SL1100 - POV155 closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | S01AP1030 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | comando | 0 |  | 12 |  | 12.1.4.5 | 31 | 31 | DO |  |  | C | 12.1.4 | CAP1156 extract. dust SL1100 - POV155 closed |  | CAP1156 | P82 | CAP | 1156 |  | _ | 11 | ZAL | P82CAP1156_ZAL | ok | [5 empty] | 0
ID-S01AP1030-00764 | 764 |  | P82CY1100_YLRE | conveyor CY1100 dust from filter - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.3 | 1 | 6 | DI |  |  | C | 12.1.3 | CY1100 dust from filter - in remote |  | CY1100 | P82 | CY | 1100 |  | _ | 10 | YLRE | P82CY1100_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00765 | 765 |  | P82CY1100_YLH | conveyor CY1100 dust from filter - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.3 | 2 | 6 | DI |  |  | C | 12.1.3 | CY1100 dust from filter - in running |  | CY1100 | P82 | CY | 1100 |  | _ | 10 | YLH | P82CY1100_YLH | ok | [5 empty] | 0
ID-S01AP1030-00766 | 766 |  | P82CY1100_YSG | conveyor CY1100 dust from filter - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.3 | 3 | 6 | DI |  |  | C | 12.1.3 | CY1100 dust from filter - supply fault |  | CY1100 | P82 | CY | 1100 |  | _ | 10 | YSG | P82CY1100_YSG | ok | [5 empty] | 0
ID-S01AP1030-00767 | 767 |  | P82CY1100_HSH | conveyor CY1100 dust from filter - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 8 | 24 | DO |  |  | C | 12.1.3 | CY1100 dust from filter - start/stop |  | CY1100 | P82 | CY | 1100 |  | _ | 10 | HSH | P82CY1100_HSH | ok | [5 empty] | 0
ID-S01AP1030-00768 | 768 |  | P82CY1101_YLRE | conveyor CY1101 dust to bucket elev. - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.3 | 4 | 6 | DI |  |  | C | 12.1.3 | CY1101 dust to bucket elev. - in remote |  | CY1101 | P82 | CY | 1101 |  | _ | 10 | YLRE | P82CY1101_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00769 | 769 |  | P82CY1101_YLH | conveyor CY1101 dust to bucket elev. - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.3 | 5 | 6 | DI |  |  | C | 12.1.3 | CY1101 dust to bucket elev. - in running |  | CY1101 | P82 | CY | 1101 |  | _ | 10 | YLH | P82CY1101_YLH | ok | [5 empty] | 0
ID-S01AP1030-00770 | 770 |  | P82CY1101_YSG | conveyor CY1101 dust to bucket elev. - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.3 | 6 | 6 | DI |  |  | C | 12.1.3 | CY1101 dust to bucket elev. - supply fault |  | CY1101 | P82 | CY | 1101 |  | _ | 10 | YSG | P82CY1101_YSG | ok | [5 empty] | 0
ID-S01AP1030-00771 | 771 |  | P82CY1101_HSH | conveyor CY1101 dust to bucket elev. - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 9 | 24 | DO |  |  | C | 12.1.3 | CY1101 dust to bucket elev. - start/stop |  | CY1101 | P82 | CY | 1101 |  | _ | 10 | HSH | P82CY1101_HSH | ok | [5 empty] | 0
ID-S01AP1030-00772 | 772 |  | P82EH1110_YLH | elec.heater EH1110 dust CY1100 SL1150 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 1 | 24 | DI |  |  | C | 12.1.3 | EH1110 dust CY1100 SL1150 - in running |  | EH1110 | P82 | EH | 1110 |  | _ | 10 | YLH | P82EH1110_YLH | ok | [5 empty] | 0
ID-S01AP1030-00773 | 773 |  | P82EH1110_YSG | elec.heater EH1110 dust CY1100 SL1150 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 2 | 24 | DI |  |  | C | 12.1.3 | EH1110 dust CY1100 SL1150 - supply fault |  | EH1110 | P82 | EH | 1110 |  | _ | 10 | YSG | P82EH1110_YSG | ok | [5 empty] | 0
ID-S01AP1030-00774 | 774 |  | P82EH1110_HSH | elec.heater EH1110 dust CY1100 SL1150 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 10 | 24 | DO |  |  | C | 12.1.3 | EH1110 dust CY1100 SL1150 - start/stop |  | EH1110 | P82 | EH | 1110 |  | _ | 10 | HSH | P82EH1110_HSH | ok | [5 empty] | 0
ID-S01AP1030-00775 | 775 |  | P82EH1111_YLH | elec.heater EH1111 dust CY1101 SL1150 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 3 | 24 | DI |  |  | C | 12.1.3 | EH1111 dust CY1101 SL1150 - in running |  | EH1111 | P82 | EH | 1111 |  | _ | 10 | YLH | P82EH1111_YLH | ok | [5 empty] | 0
ID-S01AP1030-00776 | 776 |  | P82EH1111_YSG | elec.heater EH1111 dust CY1101 SL1150 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 4 | 24 | DI |  |  | C | 12.1.3 | EH1111 dust CY1101 SL1150 - supply fault |  | EH1111 | P82 | EH | 1111 |  | _ | 10 | YSG | P82EH1111_YSG | ok | [5 empty] | 0
ID-S01AP1030-00777 | 777 |  | P82EH1111_HSH | elec.heater EH1111 dust CY1101 SL1150 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 11 | 24 | DO |  |  | C | 12.1.3 | EH1111 dust CY1101 SL1150 - start/stop |  | EH1111 | P82 | EH | 1111 |  | _ | 10 | HSH | P82EH1111_HSH | ok | [5 empty] | 0
ID-S01AP1030-00778 | 778 |  | P82EH1112_YLH | elec.heater EH1112 dust EL1102 SL1150 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 5 | 24 | DI |  |  | C | 12.1.3 | EH1112 dust EL1102 SL1150 - in running |  | EH1112 | P82 | EH | 1112 |  | _ | 10 | YLH | P82EH1112_YLH | ok | [5 empty] | 0
ID-S01AP1030-00779 | 779 |  | P82EH1112_YSG | elec.heater EH1112 dust EL1102 SL1150 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 6 | 24 | DI |  |  | C | 12.1.3 | EH1112 dust EL1102 SL1150 - supply fault |  | EH1112 | P82 | EH | 1112 |  | _ | 10 | YSG | P82EH1112_YSG | ok | [5 empty] | 0
ID-S01AP1030-00780 | 780 |  | P82EH1112_HSH | elec.heater EH1112 dust EL1102 SL1150 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 12 | 24 | DO |  |  | C | 12.1.3 | EH1112 dust EL1102 SL1150 - start/stop |  | EH1112 | P82 | EH | 1112 |  | _ | 10 | HSH | P82EH1112_HSH | ok | [5 empty] | 0
ID-S01AP1030-00781 | 781 |  | P82EH1160_YLH | elec.heater EH1160 dust silos SL1150 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 7 | 24 | DI |  |  | F | 12.1.3 | EH1160 dust silos SL1150 - in running |  | EH1160 | P82 | EH | 1160 |  | _ | 10 | YLH | P82EH1160_YLH | ok | [5 empty] | 0
ID-S01AP1030-00782 | 782 |  | P82EH1160_YSG | elec.heater EH1160 dust silos SL1150 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 8 | 24 | DI |  |  | F | 12.1.3 | EH1160 dust silos SL1150 - supply fault |  | EH1160 | P82 | EH | 1160 |  | _ | 10 | YSG | P82EH1160_YSG | ok | [5 empty] | 0
ID-S01AP1030-00783 | 783 |  | P82EH1160_HSH | elec.heater EH1160 dust silos SL1150 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 13 | 24 | DO |  |  | F | 12.1.3 | EH1160 dust silos SL1150 - start/stop |  | EH1160 | P82 | EH | 1160 |  | _ | 10 | HSH | P82EH1160_HSH | ok | [5 empty] | 0
ID-S01AP1030-00784 | 784 |  | P82EH1161_YLH | elec.heater EH1161 dust hopper SL1150 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 9 | 24 | DI |  |  | F | 12.1.3 | EH1161 dust hopper SL1150 - in running |  | EH1161 | P82 | EH | 1161 |  | _ | 10 | YLH | P82EH1161_YLH | ok | [5 empty] | 0
ID-S01AP1030-00785 | 785 |  | P82EH1161_YSG | elec.heater EH1161 dust hopper SL1150 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 10 | 24 | DI |  |  | F | 12.1.3 | EH1161 dust hopper SL1150 - supply fault |  | EH1161 | P82 | EH | 1161 |  | _ | 10 | YSG | P82EH1161_YSG | ok | [5 empty] | 0
ID-S01AP1030-00786 | 786 |  | P82EH1161_HSH | elec.heater EH1161 dust hopper SL1150 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 14 | 24 | DO |  |  | F | 12.1.3 | EH1161 dust hopper SL1150 - start/stop |  | EH1161 | P82 | EH | 1161 |  | _ | 10 | HSH | P82EH1161_HSH | ok | [5 empty] | 0
ID-S01AP1030-00787 | 787 |  | P82EH1162_YLH | elec.heater EH1162 dust conveyor SW1154 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 11 | 24 | DI |  |  | F | 12.1.3 | EH1162 dust conveyor SW1154 - in running |  | EH1162 | P82 | EH | 1162 |  | _ | 10 | YLH | P82EH1162_YLH | ok | [5 empty] | 0
ID-S01AP1030-00788 | 788 |  | P82EH1162_YSG | elec.heater EH1162 dust conveyor SW1154 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 12 | 24 | DI |  |  | F | 12.1.3 | EH1162 dust conveyor SW1154 - supply fault |  | EH1162 | P82 | EH | 1162 |  | _ | 10 | YSG | P82EH1162_YSG | ok | [5 empty] | 0
ID-S01AP1030-00789 | 789 |  | P82EH1162_HSH | elec.heater EH1162 dust conveyor SW1154 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 15 | 24 | DO |  |  | F | 12.1.3 | EH1162 dust conveyor SW1154 - start/stop |  | EH1162 | P82 | EH | 1162 |  | _ | 10 | HSH | P82EH1162_HSH | ok | [5 empty] | 0
ID-S01AP1030-00790 | 790 |  | P82EL1102_YLRE | elevator EL1102 dust - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 13 | 24 | DI |  |  | C | 12.1.3 | EL1102 dust - in remote |  | EL1102 | P82 | EL | 1102 |  | _ | 10 | YLRE | P82EL1102_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00791 | 791 |  | P82EL1102_YLH | elevator EL1102 dust - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 14 | 24 | DI |  |  | C | 12.1.3 | EL1102 dust - in running |  | EL1102 | P82 | EL | 1102 |  | _ | 10 | YLH | P82EL1102_YLH | ok | [5 empty] | 0
ID-S01AP1030-00792 | 792 |  | P82EL1102_YSG | elevator EL1102 dust - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 15 | 24 | DI |  |  | C | 12.1.3 | EL1102 dust - supply fault |  | EL1102 | P82 | EL | 1102 |  | _ | 10 | YSG | P82EL1102_YSG | ok | [5 empty] | 0
ID-S01AP1030-00793 | 793 |  | P82EL1102_HSH | elevator EL1102 dust - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 16 | 24 | DO |  |  | C | 12.1.3 | EL1102 dust - start/stop |  | EL1102 | P82 | EL | 1102 |  | _ | 10 | HSH | P82EL1102_HSH | ok | [5 empty] | 0
ID-S01AP1030-00794 | 794 |  | P82FN1157_YLRE | fan FN1157 vent dust CV1156 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 16 | 24 | DI |  |  | C | 12.1.3 | FN1157 vent dust CV1156 - in remote |  | FN1157 | P82 | FN | 1157 |  | _ | 10 | YLRE | P82FN1157_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00795 | 795 |  | P82FN1157_YLH | fan FN1157 vent dust CV1156 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 17 | 24 | DI |  |  | C | 12.1.3 | FN1157 vent dust CV1156 - in running |  | FN1157 | P82 | FN | 1157 |  | _ | 10 | YLH | P82FN1157_YLH | ok | [5 empty] | 0
ID-S01AP1030-00796 | 796 |  | P82FN1157_YSG | fan FN1157 vent dust CV1156 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 18 | 24 | DI |  |  | C | 12.1.3 | FN1157 vent dust CV1156 - supply fault |  | FN1157 | P82 | FN | 1157 |  | _ | 10 | YSG | P82FN1157_YSG | ok | [5 empty] | 0
ID-S01AP1030-00797 | 797 |  | P82FN1157_HSH | fan FN1157 vent dust CV1156 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 17 | 24 | DO |  |  | C | 12.1.3 | FN1157 vent dust CV1156 - start/stop |  | FN1157 | P82 | FN | 1157 |  | _ | 10 | HSH | P82FN1157_HSH | ok | [5 empty] | 0
ID-S01AP1030-00798 | 798 |  | P82HV1151_ZSH | vlv. HV1151 extract. dust silos SL1150 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.6 | 11 | 17 | DI |  |  | C | 12.1.8 | HV1151 extract. dust silos SL1150 - opened |  | HV1151 | P82 | HV | 1151 |  | _ | 10 | ZSH | P82HV1151_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00799 | 799 |  | P82HV1151_YLRE | vlv. HV1151 extract. dust silos SL1150 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 |  |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | HV1151 extract. dust silos SL1150 - in remote |  | HV1151 | P82 | HV | 1151 |  | _ | 10 | YLRE | P82HV1151_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00800 | 800 |  | P82HV1151_YSA | vlv. HV1151 extract. dust silos SL1150 - com.alarm |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 |  |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | HV1151 extract. dust silos SL1150 - com.alarm |  | HV1151 | P82 | HV | 1151 |  | _ | 10 | YSA | P82HV1151_YSA | ok | [5 empty] | 0
ID-S01AP1030-00801 | 801 |  | P82HV1151_HSH | vlv. HV1151 extract. dust silos SL1150 - enable |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 |  |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | HV1151 extract. dust silos SL1150 - enable |  | HV1151 | P82 | HV | 1151 |  | _ | 10 | HSH | P82HV1151_HSH | ok | [5 empty] | 0
ID-S01AP1030-00802 | 802 |  | P82LB1156_YLRE | load.bell. LB1156 dust silos SL1150 - in remote |  | 1 | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 19 | 24 | DI |  |  | C | 12.1.3 | LB1156 dust silos SL1150 - in remote |  | LB1156 | P82 | LB | 1156 |  | _ | 10 | YLRE | P82LB1156_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00803 | 803 |  | P82LB1156_YLH | load.bell. LB1156 dust silos SL1150 - in running |  | 1 | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 20 | 24 | DI |  |  | C | 12.1.3 | LB1156 dust silos SL1150 - in running |  | LB1156 | P82 | LB | 1156 |  | _ | 10 | YLH | P82LB1156_YLH | ok | [5 empty] | 0
ID-S01AP1030-00804 | 804 |  | P82LB1156_YSG | load.bell. LB1156 dust silos SL1150 - supply fault |  | 1 | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 21 | 24 | DI |  |  | C | 12.1.3 | LB1156 dust silos SL1150 - supply fault |  | LB1156 | P82 | LB | 1156 |  | _ | 10 | YSG | P82LB1156_YSG | ok | [5 empty] | 0
ID-S01AP1030-00805 | 805 |  | P82LB1156_HSH | load.bell. LB1156 dust silos SL1150 - start/stop |  | 1 | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 18 | 24 | DO |  |  | C | 12.1.3 | LB1156 dust silos SL1150 - start/stop |  | LB1156 | P82 | LB | 1156 |  | _ | 10 | HSH | P82LB1156_HSH | ok | [5 empty] | 0
ID-S01AP1030-00806 | 806 |  | P82LSH1101 | lev. H LSH1101 dust emergency discharge |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.8.6 | 12 | 17 | DI |  |  | D | 12.1.8 | H LSH1101 dust emergency discharge |  | H | P82 | LSH | 1101 |  |  |  |  | P82LSH1101 | ok | [5 empty] | 0
ID-S01AP1030-00807 | 807 |  | P82LSHH1150 | lev. HH LSHH1150 dust silos SL1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.8.6 | 13 | 17 | DI |  |  | D | 12.1.8 | HH LSHH1150 dust silos SL1150 |  | HH | P82 | LSHH | 1150 |  |  |  |  | P82LSHH1150 | ok | [5 empty] | 0
ID-S01AP1030-00808 | 808 |  | P82LSLL1150 | lev. LL LSLL1150 dust silos SL1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPDT 4 wires | false | = | active | 0 |  | 12 |  | 12.1.8.6 | 14 | 17 | DI |  |  | D | 12.1.8 | LL LSLL1150 dust silos SL1150 |  | LL | P82 | LSLL | 1150 |  |  |  |  | P82LSLL1150 | ok | [5 empty] | 0
ID-S01AP1030-00809 | 809 |  | P82LI1150 | lev. LT1150 dust silos SL1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 100 | % |  | 12 |  | 12.1.8.3 | 15 | 16 | AI |  |  | C | 12.1.8 | LT1150 dust silos SL1150 |  | LT1150 | P82 | LI | 1150 |  |  |  |  | P82LI1150 | ok |  |  |  | 0 | 100 | %
ID-S01AP1030-00810 | 810 |  | P82POV1103_ZSH | vlv. POV1103 dust to emergency discharge - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.6 | 15 | 17 | DI |  |  | C | 12.1.8 | POV1103 dust to emergency discharge - opened |  | POV1103 | P82 | POV | 1103 |  | _ | 11 | ZSH | P82POV1103_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00811 | 811 |  | P82POV1103_HSH | vlv. POV1103 dust to emergency discharge - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 26 | 32 | DO |  |  | C | 12.1.7 | POV1103 dust to emergency discharge - open |  | POV1103 | P82 | POV | 1103 |  | _ | 11 | HSH | P82POV1103_HSH | ok | [5 empty] | 0
ID-S01AP1030-00812 | 812 |  | P82POV1103_HSL | vlv. POV1103 dust to emergency discharge - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 27 | 32 | DO |  |  | C | 12.1.7 | POV1103 dust to emergency discharge - close |  | POV1103 | P82 | POV | 1103 |  | _ | 11 | HSL | P82POV1103_HSL | ok | [5 empty] | 0
ID-S01AP1030-00813 | 813 |  | P82POV1150_ZSL | vlv. POV1150 vent dust CV1156 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | POV1150 vent dust CV1156 - closed |  | POV1150 | P82 | POV | 1150 |  | _ | 11 | ZSL | P82POV1150_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00814 | 814 |  | P82POV1150_HSL | vlv. POV1150 vent dust CV1156 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | POV1150 vent dust CV1156 - close |  | POV1150 | P82 | POV | 1150 |  | _ | 11 | HSL | P82POV1150_HSL | ok | [5 empty] | 0
ID-S01AP1030-00815 | 815 |  | P82POV1152_ZSH | vlv. POV1152 extract. dust silos SL1150 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.6 | 16 | 17 | DI |  |  | C | 12.1.8 | POV1152 extract. dust silos SL1150 - opened |  | POV1152 | P82 | POV | 1152 |  | _ | 11 | ZSH | P82POV1152_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00816 | 816 |  | P82POV1152_ZSL | vlv. POV1152 extract. dust silos SL1150 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.8.6 | 17 | 17 | DI |  |  | C | 12.1.8 | POV1152 extract. dust silos SL1150 - closed |  | POV1152 | P82 | POV | 1152 |  | _ | 11 | ZSL | P82POV1152_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00817 | 817 |  | P82POV1152_HSH | vlv. POV1152 extract. dust silos SL1150 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | P82LP1152 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.3.4 | 19 | 24 | DO |  |  | C | 12.1.3 | POV1152 extract. dust silos SL1150 - open |  | POV1152 | P82 | POV | 1152 |  | _ | 11 | HSH | P82POV1152_HSH | ok | [5 empty] | 0
ID-S01AP1030-00818 | 818 |  | P82POV1152_HSL | vlv. POV1152 extract. dust silos SL1150 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | P82LP1152 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.3.4 | 20 | 24 | DO |  |  | C | 12.1.3 | POV1152 extract. dust silos SL1150 - close |  | POV1152 | P82 | POV | 1152 |  | _ | 11 | HSL | P82POV1152_HSL | ok | [5 empty] | 0
ID-S01AP1030-00819 | 819 |  | P82POV1155_ZSH | vlv. POV1155 dust outlet SW1154 - opened |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.6.8 | 12 | 25 | DI |  |  | C | 12.1.6 | POV1155 dust outlet SW1154 - opened |  | POV1155 | P82 | POV | 1155 |  | _ | 11 | ZSH | P82POV1155_ZSH | ok | [5 empty] | 0
ID-S01AP1030-00820 | 820 |  | P82POV1155_ZSL | vlv. POV1155 dust outlet SW1154 - closed |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.6.8 | 13 | 25 | DI |  |  | C | 12.1.6 | POV1155 dust outlet SW1154 - closed |  | POV1155 | P82 | POV | 1155 |  | _ | 11 | ZSL | P82POV1155_ZSL | ok | [5 empty] | 0
ID-S01AP1030-00821 | 821 |  | P82POV1155_HSH | vlv. POV1155 dust outlet SW1154 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | P82LP1152 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.3.4 | 21 | 24 | DO |  |  | C | 12.1.3 | POV1155 dust outlet SW1154 - open |  | POV1155 | P82 | POV | 1155 |  | _ | 11 | HSH | P82POV1155_HSH | ok | [5 empty] | 0
ID-S01AP1030-00822 | 822 |  | P82POV1155_HSL | vlv. POV1155 dust outlet SW1154 - close |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | P82LP1152 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.3.4 | 22 | 24 | DO |  |  | C | 12.1.3 | POV1155 dust outlet SW1154 - close |  | POV1155 | P82 | POV | 1155 |  | _ | 11 | HSL | P82POV1155_HSL | ok | [5 empty] | 0
ID-S01AP1030-00823 | 823 |  | P82BAC1153B_YLRE | bin activ. BAC1153B dust silos SL1151 - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active |  |  | 12 | B | 12.1.4.7 | 1 | 3 | DI |  |  | A | 12.1.4 | activ. BAC1153B dust silos SL1151 - in remote |  | activ. | P82 | BAC | 1153 | B | _ | 12 | YLRE | P82BAC1153B_YLRE | ok
ID-S01AP1030-00824 | 824 |  | P82BAC1153B_YLH | bin activ. BAC1153B dust silos SL1151 - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active |  |  | 12 | B | 12.1.4.7 | 2 | 3 | DI |  |  | A | 12.1.4 | activ. BAC1153B dust silos SL1151 - in running |  | activ. | P82 | BAC | 1153 | B | _ | 12 | YLH | P82BAC1153B_YLH | ok
ID-S01AP1030-00825 | 825 |  | P82BAC1153B_YSG | bin activ. BAC1153B dust silos SL1151 - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active |  |  | 12 | B | 12.1.4.7 | 3 | 3 | DI |  |  | A | 12.1.4 | activ. BAC1153B dust silos SL1151 - supply fault |  | activ. | P82 | BAC | 1153 | B | _ | 12 | YSG | P82BAC1153B_YSG | ok
ID-S01AP1030-00826 | 826 |  | P82BAC1153B_HSH | bin activ. BAC1153B dust silos SL1151 - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start |  |  | 12 |  | 12.1.3.4 | 23 | 24 | DO |  |  | A | 12.1.3 | activ. BAC1153B dust silos SL1151 - start/stop |  | activ. | P82 | BAC | 1153 | B | _ | 12 | HSH | P82BAC1153B_HSH | ok
ID-S01AP1030-00827 | 827 |  | P82PSHH1150 | pres. HH PSHH1150 dust compr.air FF1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 14 | 25 | DI |  |  | C | 12.1.6 | HH PSHH1150 dust compr.air FF1150 |  | HH | P82 | PSHH | 1150 |  |  |  |  | P82PSHH1150 | ok | [5 empty] | 0
ID-S01AP1030-00828 | 828 |  | P82PSL1351 | pres. L PSL1351 dust compr.air PRV1351 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 15 | 25 | DI |  |  | C | 12.1.6 | L PSL1351 dust compr.air PRV1351 |  | L | P82 | PSL | 1351 |  |  |  |  | P82PSL1351 | ok | [5 empty] | 0
ID-S01AP1030-00829 | 829 |  | P82SOV1300_HSH | vlv. SOV1300 dust compr.air EL1102 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-001 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 28 | 32 | DO |  |  | C | 12.1.7 | SOV1300 dust compr.air EL1102 - open |  | SOV1300 | P82 | SOV | 1300 |  | _ | 11 | HSH | P82SOV1300_HSH | ok | [5 empty] | 0
ID-S01AP1030-00830 | 830 |  | P82SOV1301_HSH | vlv. SOV1301 dust compr.air EL1102 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 29 | 32 | DO |  |  | C | 12.1.7 | SOV1301 dust compr.air EL1102 - open |  | SOV1301 | P82 | SOV | 1301 |  | _ | 11 | HSH | P82SOV1301_HSH | ok | [5 empty] | 0
ID-S01AP1030-00831 | 831 |  | P82SOV1357_HSH | vlv. SOV1357 fluid dust compr.air PRV1357 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 30 | 32 | DO |  |  | C | 12.1.7 | SOV1357 fluid dust compr.air PRV1357 - open |  | SOV1357 | P82 | SOV | 1357 |  | _ | 11 | HSH | P82SOV1357_HSH | ok | [5 empty] | 0
ID-S01AP1030-00832 | 832 |  | P82SOV1358_HSH | vlv. SOV1358 fluid dust compr.air PRV1358 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 31 | 32 | DO |  |  | C | 12.1.7 | SOV1358 fluid dust compr.air PRV1358 - open |  | SOV1358 | P82 | SOV | 1358 |  | _ | 11 | HSH | P82SOV1358_HSH | ok | [5 empty] | 0
ID-S01AP1030-00833 | 833 |  | P82SOV1359_HSH | vlv. SOV1359 fluid dust compr.air PRV1359 - open |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 12 |  | 12.1.7.4 | 32 | 32 | DO |  |  | C | 12.1.7 | SOV1359 fluid dust compr.air PRV1359 - open |  | SOV1359 | P82 | SOV | 1359 |  | _ | 11 | HSH | P82SOV1359_HSH | ok | [5 empty] | 0
ID-S01AP1030-00834 | 834 |  | P82SSL1100 | speed L SSL1100 dust conveyor CY1100 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 16 | 25 | DI |  |  | C | 12.1.6 | L SSL1100 dust conveyor CY1100 |  | L | P82 | SSL | 1100 |  |  |  |  | P82SSL1100 | ok | [5 empty] | 0
ID-S01AP1030-00835 | 835 |  | P82SSL1101 | speed L SSL1101 dust conveyor CY1101 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 17 | 25 | DI |  |  | C | 12.1.6 | L SSL1101 dust conveyor CY1101 |  | L | P82 | SSL | 1101 |  |  |  |  | P82SSL1101 | ok | [5 empty] | 0
ID-S01AP1030-00836 | 836 |  | P82SSL1102 | speed L SSL1102 dust conveyor EL1102 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 18 | 25 | DI |  |  | C | 12.1.6 | L SSL1102 dust conveyor EL1102 |  | L | P82 | SSL | 1102 |  |  |  |  | P82SSL1102 | ok | [5 empty] | 0
ID-S01AP1030-00837 | 837 |  | P82SSL1154 | speed L SSL1154 dust conveyor SW1154 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 19 | 25 | DI |  |  | C | 12.1.6 | L SSL1154 dust conveyor SW1154 |  | L | P82 | SSL | 1154 |  |  |  |  | P82SSL1154 | ok | [5 empty] | 0
ID-S01AP1030-00838 | 838 |  | P82SW1154_YLRE | screw conv. SW1154 extract. dust - in remote |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 22 | 24 | DI |  |  | C | 12.1.3 | conv. SW1154 extract. dust - in remote |  | conv. | P82 | SW | 1154 |  | _ | 10 | YLRE | P82SW1154_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00839 | 839 |  | P82SW1154_YLH | screw conv. SW1154 extract. dust - in running |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 12 |  | 12.1.3.2 | 23 | 24 | DI |  |  | C | 12.1.3 | conv. SW1154 extract. dust - in running |  | conv. | P82 | SW | 1154 |  | _ | 10 | YLH | P82SW1154_YLH | ok | [5 empty] | 0
ID-S01AP1030-00840 | 840 |  | P82SW1154_YSG | screw conv. SW1154 extract. dust - supply fault |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.3.2 | 24 | 24 | DI |  |  | C | 12.1.3 | conv. SW1154 extract. dust - supply fault |  | conv. | P82 | SW | 1154 |  | _ | 10 | YSG | P82SW1154_YSG | ok | [5 empty] | 0
ID-S01AP1030-00841 | 841 |  | P82SW1154_HSH | screw conv. SW1154 extract. dust - start/stop |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | G12MCC1001 |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 12 |  | 12.1.3.4 | 24 | 24 | DO |  |  | C | 12.1.3 | conv. SW1154 extract. dust - start/stop |  | conv. | P82 | SW | 1154 |  | _ | 10 | HSH | P82SW1154_HSH | ok | [5 empty] | 0
ID-S01AP1030-00842 | 842 |  | P82LB1156_YLRE | load.bell. LB1156 dust silos SL1150 - in remote |  | 1 | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 |  |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LB1156 dust silos SL1150 - in remote |  | LB1156 | P82 | LB | 1156 |  | _ | 10 | YLRE | P82LB1156_YLRE | ok | [5 empty] | 0
ID-S01AP1030-00843 | 843 |  | P82LB1156_YLH | load.bell. LB1156 dust silos SL1150 - in running |  | 1 | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 |  |  | S01AP1030 |  |  |  |  | DI | SPST | true | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LB1156 dust silos SL1150 - in running |  | LB1156 | P82 | LB | 1156 |  | _ | 10 | YLH | P82LB1156_YLH | ok | [5 empty] | 0
ID-S01AP1030-00844 | 844 |  | P82LB1156_YSG | load.bell. LB1156 dust silos SL1150 - supply fault |  | 1 | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 |  |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LB1156 dust silos SL1150 - supply fault |  | LB1156 | P82 | LB | 1156 |  | _ | 10 | YSG | P82LB1156_YSG | ok | [5 empty] | 0
ID-S01AP1030-00845 | 845 |  | P82LB1156_HSH | load.bell. LB1156 dust silos SL1150 - start/stop |  | 1 | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 |  |  | S01AP1030 |  |  |  |  | DO | RELAY | true | → | start | 0 |  |  |  |  | 0 | 0 | #N/A |  | D | C |  | LB1156 dust silos SL1150 - start/stop |  | LB1156 | P82 | LB | 1156 |  | _ | 10 | HSH | P82LB1156_HSH | ok | [5 empty] | 0
ID-S01AP1030-00846 | 846 |  | P82TSH1110 | temp. H TSH1110 dust Heater EH1110 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P32-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 20 | 25 | DI |  |  | C | 12.1.6 | H TSH1110 dust Heater EH1110 |  | H | P82 | TSH | 1110 |  |  |  |  | P82TSH1110 | ok | [5 empty] | 0
ID-S01AP1030-00847 | 847 |  | P82TSH1111 | temp. H TSH1111 dust Heater EH1111 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P32-JBD-1-003 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 21 | 25 | DI |  |  | C | 12.1.6 | H TSH1111 dust Heater EH1111 |  | H | P82 | TSH | 1111 |  |  |  |  | P82TSH1111 | ok | [5 empty] | 0
ID-S01AP1030-00848 | 848 |  | P82TSH1112 | temp. H TSH1112 dust Heater EH1112 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 22 | 25 | DI |  |  | C | 12.1.6 | H TSH1112 dust Heater EH1112 |  | H | P82 | TSH | 1112 |  |  |  |  | P82TSH1112 | ok | [5 empty] | 0
ID-S01AP1030-00849 | 849 |  | P82TSH1160 | temp. H TSH1160 dust silos Heater EH1160 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 23 | 25 | DI |  |  | C | 12.1.6 | H TSH1160 dust silos Heater EH1160 |  | H | P82 | TSH | 1160 |  |  |  |  | P82TSH1160 | ok | [5 empty] | 0
ID-S01AP1030-00850 | 850 |  | P82TSH1161 | temp. H TSH1161 dust Heater EH1161 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 24 | 25 | DI |  |  | C | 12.1.6 | H TSH1161 dust Heater EH1161 |  | H | P82 | TSH | 1161 |  |  |  |  | P82TSH1161 | ok | [5 empty] | 0
ID-S01AP1030-00851 | 851 |  | P82TSH1162 | temp. H TSH1162 dust Heater EH1162 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBD-1-002 |  | S01AP1030 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 12 |  | 12.1.6.8 | 25 | 25 | DI |  |  | C | 12.1.6 | H TSH1162 dust Heater EH1162 |  | H | P82 | TSH | 1162 |  |  |  |  | P82TSH1162 | ok | [5 empty] | 0
ID-S01AP1030-00852 | 852 |  | P82WI1150 | weight WT1150 dust silos SL1150 |  |  | FLUE GAS CLEANING 1 | CHN1 TDZ2 P82 DP01 | CHN1-TDZ2-P82-JBA-1-001 |  | S01AP1030 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ¸ | 200 | ton | 220 Vac / .. | 12 |  | 12.1.8.3 | 16 | 16 | AI |  |  | H | 12.1.8 | WT1150 dust silos SL1150 |  | WT1150 | P82 | WI | 1150 |  |  |  |  | P82WI1150 | ok |  |  |  | 0 | 200 | ton
ID-S01AP1020-00001 | 1 |  | P23CY1003_YLRE | conveyor CY1003 was. from bunker - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YLRE | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 1 | 32 | DI |  |  | 0 | 11.1.1 | CY1003 was. from bunker - in remote |  | CY1003 | P23 | CY | 1003 |  | _ | 10 | YLRE | P23CY1003_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00002 | 2 |  | P23CY1003_YLH | conveyor CY1003 was. from bunker - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YLH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 2 | 32 | DI |  |  | 0 | 11.1.1 | CY1003 was. from bunker - in running |  | CY1003 | P23 | CY | 1003 |  | _ | 10 | YLH | P23CY1003_YLH | ok | [5 empty] | 0
ID-S01AP1020-00003 | 3 |  | P23CY1003_YS | conveyor CY1003 was. from bunker - gen.fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.1.3 | 3 | 32 | DI |  |  | 0 | 11.1.1 | CY1003 was. from bunker - gen.fault |  | CY1003 | P23 | CY | 1003 |  | _ | 10 | YS | P23CY1003_YS | ok | [5 empty] | 0
ID-S01AP1020-00004 | 4 |  | P23CY1003_HSH | conveyor CY1003 was. from bunker - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 1 | 30 | DO |  |  | 0 | 11.1.1 | CY1003 was. from bunker - start/stop |  | CY1003 | P23 | CY | 1003 |  | _ | 10 | HSH | P23CY1003_HSH | ok | [5 empty] | 0
ID-S01AP1020-00005 | 5 |  | P23CY1003_SI | conveyor CY1003 was. from bunker - speed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | ST | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.1.7 | 1 | 13 | AI |  |  | 0 | 11.1.1 | CY1003 was. from bunker - speed |  | CY1003 | P23 | CY | 1003 |  | _ | 10 | SI | P23CY1003_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-00006 | 6 |  | P23CY1003_II | conveyor CY1003 was. from bunker - current |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | IT | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 11 |  | 11.1.1.7 | 2 | 13 | AI |  |  | 0 | 11.1.1 | CY1003 was. from bunker - current |  | CY1003 | P23 | CY | 1003 |  | _ | 10 | II | P23CY1003_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1020-00007 | 7 |  | P23CY1003_SY | conveyor CY1003 was. from bunker - req.speed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | SY | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.1.8 | 1 | 8 | AO |  |  | 0 | 11.1.1 | CY1003 was. from bunker - req.speed |  | CY1003 | P23 | CY | 1003 |  | _ | 10 | SY | P23CY1003_SY | ok |  |  |  | 0 |  | %
ID-S01AP1020-00008 | 8 | P23LP1010_YSA | P23LP1010_YSA-1 | loc.pan. LP1010 elevator drums - truck ready |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | OPS_7 | YSA | DI | SPST | true | = | 0 | 0 |  | 11 |  | 11.1.1.3 | 4 | 32 | DI |  |  | 0 | 11.1.1 | LP1010 elevator drums - truck ready |  | LP1010 | P23 | LP | 1010 |  | _ | 10 | YSA-1 | P23LP1010_YSA-1 | ok | [5 empty] | 0
ID-S01AP1020-00009 | 9 | P23LP1010_YSA | P23LP1010_YSA-2 | loc.pan. LP1010 elevator drums - sequence started |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | OPS_7 | YSA | DI | SPST | true | = | 0 | 0 |  | 11 |  | 11.1.1.3 | 5 | 32 | DI |  |  | 0 | 11.1.1 | LP1010 elevator drums - sequence started |  | LP1010 | P23 | LP | 1010 |  | _ | 10 | YSA-2 | P23LP1010_YSA-2 | ok | [5 empty] | 0
ID-S01AP1020-00010 | 10 | P23LP1010_YSA | P23LP1010_YSA-3 | loc.pan. LP1010 elevator drums - excessive weight |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | OPS_7 | YSA | DI | SPST | true | = | 0 | 0 |  | 11 |  | 11.1.1.3 | 6 | 32 | DI |  |  | 0 | 11.1.1 | LP1010 elevator drums - excessive weight |  | LP1010 | P23 | LP | 1010 |  | _ | 10 | YSA-3 | P23LP1010_YSA-3 | ok | [5 empty] | 0
ID-S01AP1020-00011 | 11 | P23LP1010_YSA | P23LP1010_YSA-4 | loc.pan. LP1010 elevator drums - arrival at the upper floor | 59 |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | OPS_7 | YSA | DI | SPST | true | = | 0 | 0 |  | 11 |  | 11.1.1.3 | 7 | 32 | DI |  |  | 0 | 11.1.1 | LP1010 elevator drums - arrival at the upper floor |  | LP1010 | P23 | LP | 1010 |  | _ | 10 | YSA-4 | P23LP1010_YSA-4 | ok | [5 empty] | 0
ID-S01AP1020-00012 | 12 | P23LP1010_YSA | P23LP1010_YSA-5 | loc.pan. LP1010 elevator drums - charge carried out |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | OPS_7 | YSA | DI | SPST | true | = | 0 | 0 |  | 11 |  | 11.1.1.3 | 8 | 32 | DI |  |  | 0 | 11.1.1 | LP1010 elevator drums - charge carried out |  | LP1010 | P23 | LP | 1010 |  | _ | 10 | YSA-5 | P23LP1010_YSA-5 | ok | [5 empty] | 0
ID-S01AP1020-00013 | 13 | P23LP1010_YSA | P23LP1010_YSA-6 | loc.pan. LP1010 elevator drums - stem on the elevator |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | OPS_7 | YSA | DI | SPST | true | = | 0 | 0 |  | 11 |  | 11.1.1.3 | 9 | 32 | DI |  |  | 0 | 11.1.1 | LP1010 elevator drums - stem on the elevator |  | LP1010 | P23 | LP | 1010 |  | _ | 10 | YSA-6 | P23LP1010_YSA-6 | ok | [5 empty] | 0
ID-S01AP1020-00014 | 14 | P23LP1010_HSH | P23LP1010_HSH-1 | loc.pan. LP1010 elevator drums - enabling at the exhaust | 56 |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | OPS_7 | HSH | DO | RELAY | true | → | 0 | 0 |  | 11 |  | 11.1.1.4 | 2 | 30 | DO |  |  | 0 | 11.1.1 | LP1010 elevator drums - enabling at the exhaust |  | LP1010 | P23 | LP | 1010 |  | _ | 10 | HSH-1 | P23LP1010_HSH-1 | ok | [5 empty] | 0
ID-S01AP1020-00015 | 15 | P23LP1010_HSH | P23LP1010_HSH-2 | loc.pan. LP1010 elevator drums - request loading |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | OPS_7 | HSH | DO | RELAY | true | → | 0 | 0 |  | 11 |  | 11.1.1.4 | 3 | 30 | DO |  |  | 0 | 11.1.1 | LP1010 elevator drums - request loading |  | LP1010 | P23 | LP | 1010 |  | _ | 10 | HSH-2 | P23LP1010_HSH-2 | ok | [5 empty] | 0
ID-S01AP1020-00016 | 16 | P23LP1010_HSH | P23LP1010_HSH-3 | loc.pan. LP1010 elevator drums - load door open |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | OPS_7 | HSH | DO | RELAY | true | → | 0 | 0 |  | 11 |  | 11.1.1.4 | 4 | 30 | DO |  |  | 0 | 11.1.1 | LP1010 elevator drums - load door open |  | LP1010 | P23 | LP | 1010 |  | _ | 10 | HSH-3 | P23LP1010_HSH-3 | ok | [5 empty] | 0
ID-S01AP1020-00017 | 17 |  | P23RK1002_YLRE | rot.kiln RK1002 main motor - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YLRE | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 10 | 32 | DI |  |  | 0 | 11.1.1 | RK1002 main motor - in remote |  | RK1002 | P23 | RK | 1002 |  | _ | 10 | YLRE | P23RK1002_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00018 | 18 |  | P23RK1002_YLH | rot.kiln RK1002 main motor - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YLH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 11 | 32 | DI |  |  | 0 | 11.1.1 | RK1002 main motor - in running |  | RK1002 | P23 | RK | 1002 |  | _ | 10 | YLH | P23RK1002_YLH | ok | [5 empty] | 0
ID-S01AP1020-00019 | 19 |  | P23RK1002_YS | rot.kiln RK1002 main motor - gen.fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.1.3 | 12 | 32 | DI |  |  | 0 | 11.1.1 | RK1002 main motor - gen.fault |  | RK1002 | P23 | RK | 1002 |  | _ | 10 | YS | P23RK1002_YS | ok | [5 empty] | 0
ID-S01AP1020-00020 | 20 |  | P23RK1002_HSH | rot.kiln RK1002 main motor - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 5 | 30 | DO |  |  | 0 | 11.1.1 | RK1002 main motor - start/stop |  | RK1002 | P23 | RK | 1002 |  | _ | 10 | HSH | P23RK1002_HSH | ok | [5 empty] | 0
ID-S01AP1020-00021 | 21 |  | P23RK1002_SI | rot.kiln RK1002 main motor - speed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | ST | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.1.7 | 3 | 13 | AI |  |  | 0 | 11.1.1 | RK1002 main motor - speed |  | RK1002 | P23 | RK | 1002 |  | _ | 10 | SI | P23RK1002_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-00022 | 22 |  | P23RK1002_II | rot.kiln RK1002 main motor - current |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | IT | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 11 |  | 11.1.1.7 | 4 | 13 | AI |  |  | 0 | 11.1.1 | RK1002 main motor - current |  | RK1002 | P23 | RK | 1002 |  | _ | 10 | II | P23RK1002_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1020-00023 | 23 |  | P23RK1002_SY | rot.kiln RK1002 main motor - req.speed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | SY | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.1.8 | 2 | 8 | AO |  |  | 0 | 11.1.1 | RK1002 main motor - req.speed |  | RK1002 | P23 | RK | 1002 |  | _ | 10 | SY | P23RK1002_SY | ok |  |  |  | 0 |  | %
ID-S01AP1020-00024 | 24 |  | P23RK1003_YLRE | rot.kiln RK1003 auxiliary motor - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 13 | 32 | DI |  |  | 0 | 11.1.1 | RK1003 auxiliary motor - in remote |  | RK1003 | P23 | RK | 1003 |  | _ | 10 | YLRE | P23RK1003_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00025 | 25 |  | P23RK1003_YLH | rot.kiln RK1003 auxiliary motor - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 14 | 32 | DI |  |  | 0 | 11.1.1 | RK1003 auxiliary motor - in running |  | RK1003 | P23 | RK | 1003 |  | _ | 10 | YLH | P23RK1003_YLH | ok | [5 empty] | 0
ID-S01AP1020-00026 | 26 |  | P23RK1003_YSG | rot.kiln RK1003 auxiliary motor - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.1.3 | 15 | 32 | DI |  |  | 0 | 11.1.1 | RK1003 auxiliary motor - supply fault |  | RK1003 | P23 | RK | 1003 |  | _ | 10 | YSG | P23RK1003_YSG | ok | [5 empty] | 0
ID-S01AP1020-00027 | 27 |  | P23RK1003_HSH | rot.kiln RK1003 auxiliary motor - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 6 | 30 | DO |  |  | 0 | 11.1.1 | RK1003 auxiliary motor - start/stop |  | RK1003 | P23 | RK | 1003 |  | _ | 10 | HSH | P23RK1003_HSH | ok | [5 empty] | 0
ID-S01AP1020-00028 | 28 |  | P23FN1017_YLRE | fan FN1017 was.comb. primary air - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YLRE | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 16 | 32 | DI |  |  | 0 | 11.1.1 | FN1017 was.comb. primary air - in remote |  | FN1017 | P23 | FN | 1017 |  | _ | 10 | YLRE | P23FN1017_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00029 | 29 |  | P23FN1017_YLH | fan FN1017 was.comb. primary air - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YLH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 17 | 32 | DI |  |  | 0 | 11.1.1 | FN1017 was.comb. primary air - in running |  | FN1017 | P23 | FN | 1017 |  | _ | 10 | YLH | P23FN1017_YLH | ok | [5 empty] | 0
ID-S01AP1020-00030 | 30 |  | P23FN1017_YS | fan FN1017 was.comb. primary air - gen.fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.1.3 | 18 | 32 | DI |  |  | 0 | 11.1.1 | FN1017 was.comb. primary air - gen.fault |  | FN1017 | P23 | FN | 1017 |  | _ | 10 | YS | P23FN1017_YS | ok | [5 empty] | 0
ID-S01AP1020-00031 | 31 |  | P23FN1017_HSH | fan FN1017 was.comb. primary air - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 7 | 30 | DO |  |  | 0 | 11.1.1 | FN1017 was.comb. primary air - start/stop |  | FN1017 | P23 | FN | 1017 |  | _ | 10 | HSH | P23FN1017_HSH | ok | [5 empty] | 0
ID-S01AP1020-00032 | 32 |  | P23FN1017_HSK | fan FN1017 was.comb. primary air - interlock |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | HSK | DOS | RELAY | false | → | interlock | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | FN1017 was.comb. primary air - interlock |  | FN1017 | P23 | FN | 1017 |  | _ | 10 | HSK | P23FN1017_HSK | ok | [5 empty] | 0
ID-S01AP1020-00033 | 33 |  | P23FN1017_SI | fan FN1017 was.comb. primary air - speed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | ST | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.1.7 | 5 | 13 | AI |  |  | 0 | 11.1.1 | FN1017 was.comb. primary air - speed |  | FN1017 | P23 | FN | 1017 |  | _ | 10 | SI | P23FN1017_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-00034 | 34 |  | P23FN1017_II | fan FN1017 was.comb. primary air - current |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | IT | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 11 |  | 11.1.1.7 | 6 | 13 | AI |  |  | 0 | 11.1.1 | FN1017 was.comb. primary air - current |  | FN1017 | P23 | FN | 1017 |  | _ | 10 | II | P23FN1017_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1020-00035 | 35 |  | P23FN1017_SY | fan FN1017 was.comb. primary air - req.speed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | SY | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.1.8 | 3 | 8 | AO |  |  | 0 | 11.1.1 | FN1017 was.comb. primary air - req.speed |  | FN1017 | P23 | FN | 1017 |  | _ | 10 | SY | P23FN1017_SY | ok |  |  |  | 0 |  | %
ID-S01AP1020-00036 | 36 |  | P23FN1018_YLRE | fan FN1018 was.comb. - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YLRE | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 19 | 32 | DI |  |  | 0 | 11.1.1 | FN1018 was.comb. - in remote |  | FN1018 | P23 | FN | 1018 |  | _ | 10 | YLRE | P23FN1018_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00037 | 37 |  | P23FN1018_YLH | fan FN1018 was.comb. - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YLH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 20 | 32 | DI |  |  | 0 | 11.1.1 | FN1018 was.comb. - in running |  | FN1018 | P23 | FN | 1018 |  | _ | 10 | YLH | P23FN1018_YLH | ok | [5 empty] | 0
ID-S01AP1020-00038 | 38 |  | P23FN1018_YS | fan FN1018 was.comb. - gen.fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.1.3 | 21 | 32 | DI |  |  | 0 | 11.1.1 | FN1018 was.comb. - gen.fault |  | FN1018 | P23 | FN | 1018 |  | _ | 10 | YS | P23FN1018_YS | ok | [5 empty] | 0
ID-S01AP1020-00039 | 39 |  | P23FN1018_HSH | fan FN1018 was.comb. - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 8 | 30 | DO |  |  | 0 | 11.1.1 | FN1018 was.comb. - start/stop |  | FN1018 | P23 | FN | 1018 |  | _ | 10 | HSH | P23FN1018_HSH | ok | [5 empty] | 0
ID-S01AP1020-00040 | 40 |  | P23FN1018_SI | fan FN1018 was.comb. - speed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | ST | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.1.7 | 7 | 13 | AI |  |  | 0 | 11.1.1 | FN1018 was.comb. - speed |  | FN1018 | P23 | FN | 1018 |  | _ | 10 | SI | P23FN1018_SI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-00041 | 41 |  | P23FN1018_II | fan FN1018 was.comb. - current |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | IT | AI | 4/20 mA - 4W | xxx | ∕ | xxx | A |  | 11 |  | 11.1.1.7 | 8 | 13 | AI |  |  | 0 | 11.1.1 | FN1018 was.comb. - current |  | FN1018 | P23 | FN | 1018 |  | _ | 10 | II | P23FN1018_II | ok |  |  |  | xxx | xxx | A
ID-S01AP1020-00042 | 42 |  | P23FN1018_SY | fan FN1018 was.comb. - req.speed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_FC3 | SY | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.1.8 | 4 | 8 | AO |  |  | 0 | 11.1.1 | FN1018 was.comb. - req.speed |  | FN1018 | P23 | FN | 1018 |  | _ | 10 | SY | P23FN1018_SY | ok |  |  |  | 0 |  | %
ID-S01AP1020-00043 | 43 |  | P23EH1012_YLRE | elec.heater EH1012 hydr.unit HU1009 - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 22 | 32 | DI |  |  | 0 | 11.1.1 | EH1012 hydr.unit HU1009 - in remote |  | EH1012 | P23 | EH | 1012 |  | _ | 10 | YLRE | P23EH1012_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00044 | 44 |  | P23EH1012_YLH | elec.heater EH1012 hydr.unit HU1009 - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 23 | 32 | DI |  |  | 0 | 11.1.1 | EH1012 hydr.unit HU1009 - in running |  | EH1012 | P23 | EH | 1012 |  | _ | 10 | YLH | P23EH1012_YLH | ok | [5 empty] | 0
ID-S01AP1020-00045 | 45 |  | P23EH1012_YSG | elec.heater EH1012 hydr.unit HU1009 - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.1.3 | 24 | 32 | DI |  |  | 0 | 11.1.1 | EH1012 hydr.unit HU1009 - supply fault |  | EH1012 | P23 | EH | 1012 |  | _ | 10 | YSG | P23EH1012_YSG | ok | [5 empty] | 0
ID-S01AP1020-00046 | 46 |  | P23EH1012_HSH | elec.heater EH1012 hydr.unit HU1009 - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 9 | 30 | DO |  |  | 0 | 11.1.1 | EH1012 hydr.unit HU1009 - start/stop |  | EH1012 | P23 | EH | 1012 |  | _ | 10 | HSH | P23EH1012_HSH | ok | [5 empty] | 0
ID-S01AP1020-00047 | 47 |  | P23PM1010A_YLRE | pump PM1010A hydr.unit HU1009 - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.1.1 | 1 | 17 | DI |  |  | 0 | 11.1.1 | PM1010A hydr.unit HU1009 - in remote |  | PM1010A | P23 | PM | 1010 | A | _ | 11 | YLRE | P23PM1010A_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00048 | 48 |  | P23PM1010A_YLH | pump PM1010A hydr.unit HU1009 - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.1.1 | 2 | 17 | DI |  |  | 0 | 11.1.1 | PM1010A hydr.unit HU1009 - in running |  | PM1010A | P23 | PM | 1010 | A | _ | 11 | YLH | P23PM1010A_YLH | ok | [5 empty] | 0
ID-S01AP1020-00049 | 49 |  | P23PM1010A_YSG | pump PM1010A hydr.unit HU1009 - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 | A | 11.1.1.1 | 3 | 17 | DI |  |  | 0 | 11.1.1 | PM1010A hydr.unit HU1009 - supply fault |  | PM1010A | P23 | PM | 1010 | A | _ | 11 | YSG | P23PM1010A_YSG | ok | [5 empty] | 0
ID-S01AP1020-00050 | 50 |  | P23PM1010A_HSH | pump PM1010A hydr.unit HU1009 - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 10 | 30 | DO |  |  | 0 | 11.1.1 | PM1010A hydr.unit HU1009 - start/stop |  | PM1010A | P23 | PM | 1010 | A | _ | 11 | HSH | P23PM1010A_HSH | ok | [5 empty] | 0
ID-S01AP1020-00051 | 51 |  | P23PM1010B_YLRE | pump PM1010B hydr.unit HU1009 - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 1 | 20 | DI |  |  | 0 | 11.1.2 | PM1010B hydr.unit HU1009 - in remote |  | PM1010B | P23 | PM | 1010 | B | _ | 11 | YLRE | P23PM1010B_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00052 | 52 |  | P23PM1010B_YLH | pump PM1010B hydr.unit HU1009 - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 2 | 20 | DI |  |  | 0 | 11.1.2 | PM1010B hydr.unit HU1009 - in running |  | PM1010B | P23 | PM | 1010 | B | _ | 11 | YLH | P23PM1010B_YLH | ok | [5 empty] | 0
ID-S01AP1020-00053 | 53 |  | P23PM1010B_YSG | pump PM1010B hydr.unit HU1009 - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 | B | 11.1.2.8 | 3 | 20 | DI |  |  | 0 | 11.1.2 | PM1010B hydr.unit HU1009 - supply fault |  | PM1010B | P23 | PM | 1010 | B | _ | 11 | YSG | P23PM1010B_YSG | ok | [5 empty] | 0
ID-S01AP1020-00054 | 54 |  | P23PM1010B_HSH | pump PM1010B hydr.unit HU1009 - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 11 | 30 | DO |  |  | 0 | 11.1.1 | PM1010B hydr.unit HU1009 - start/stop |  | PM1010B | P23 | PM | 1010 | B | _ | 11 | HSH | P23PM1010B_HSH | ok | [5 empty] | 0
ID-S01AP1020-00055 | 55 |  | P23PM1011A_YLRE | pump PM1011A hydr.unit HU1009 - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.1.1 | 4 | 17 | DI |  |  | 0 | 11.1.1 | PM1011A hydr.unit HU1009 - in remote |  | PM1011A | P23 | PM | 1011 | A | _ | 11 | YLRE | P23PM1011A_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00056 | 56 |  | P23PM1011A_YLH | pump PM1011A hydr.unit HU1009 - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.1.1 | 5 | 17 | DI |  |  | 0 | 11.1.1 | PM1011A hydr.unit HU1009 - in running |  | PM1011A | P23 | PM | 1011 | A | _ | 11 | YLH | P23PM1011A_YLH | ok | [5 empty] | 0
ID-S01AP1020-00057 | 57 |  | P23PM1011A_YSG | pump PM1011A hydr.unit HU1009 - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 | A | 11.1.1.1 | 6 | 17 | DI |  |  | 0 | 11.1.1 | PM1011A hydr.unit HU1009 - supply fault |  | PM1011A | P23 | PM | 1011 | A | _ | 11 | YSG | P23PM1011A_YSG | ok | [5 empty] | 0
ID-S01AP1020-00058 | 58 |  | P23PM1011A_HSH | pump PM1011A hydr.unit HU1009 - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 12 | 30 | DO |  |  | 0 | 11.1.1 | PM1011A hydr.unit HU1009 - start/stop |  | PM1011A | P23 | PM | 1011 | A | _ | 11 | HSH | P23PM1011A_HSH | ok | [5 empty] | 0
ID-S01AP1020-00059 | 59 |  | P23PM1011B_YLRE | pump PM1011B hydr.unit HU1009 - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 4 | 20 | DI |  |  | 0 | 11.1.2 | PM1011B hydr.unit HU1009 - in remote |  | PM1011B | P23 | PM | 1011 | B | _ | 11 | YLRE | P23PM1011B_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00060 | 60 |  | P23PM1011B_YLH | pump PM1011B hydr.unit HU1009 - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 5 | 20 | DI |  |  | 0 | 11.1.2 | PM1011B hydr.unit HU1009 - in running |  | PM1011B | P23 | PM | 1011 | B | _ | 11 | YLH | P23PM1011B_YLH | ok | [5 empty] | 0
ID-S01AP1020-00061 | 61 |  | P23PM1011B_YSG | pump PM1011B hydr.unit HU1009 - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 | B | 11.1.2.8 | 6 | 20 | DI |  |  | 0 | 11.1.2 | PM1011B hydr.unit HU1009 - supply fault |  | PM1011B | P23 | PM | 1011 | B | _ | 11 | YSG | P23PM1011B_YSG | ok | [5 empty] | 0
ID-S01AP1020-00062 | 62 |  | P23PM1011B_HSH | pump PM1011B hydr.unit HU1009 - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 13 | 30 | DO |  |  | 0 | 11.1.1 | PM1011B hydr.unit HU1009 - start/stop |  | PM1011B | P23 | PM | 1011 | B | _ | 11 | HSH | P23PM1011B_HSH | ok | [5 empty] | 0
ID-S01AP1020-00063 | 63 |  | P23PM1027A_YLRE | pump PM1027A hydr.unit HU1009 - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.1.1 | 7 | 17 | DI |  |  | 0 | 11.1.1 | PM1027A hydr.unit HU1009 - in remote |  | PM1027A | P23 | PM | 1027 | A | _ | 11 | YLRE | P23PM1027A_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00064 | 64 |  | P23PM1027A_YLH | pump PM1027A hydr.unit HU1009 - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.1.1 | 8 | 17 | DI |  |  | 0 | 11.1.1 | PM1027A hydr.unit HU1009 - in running |  | PM1027A | P23 | PM | 1027 | A | _ | 11 | YLH | P23PM1027A_YLH | ok | [5 empty] | 0
ID-S01AP1020-00065 | 65 |  | P23PM1027A_YSG | pump PM1027A hydr.unit HU1009 - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 | A | 11.1.1.1 | 9 | 17 | DI |  |  | 0 | 11.1.1 | PM1027A hydr.unit HU1009 - supply fault |  | PM1027A | P23 | PM | 1027 | A | _ | 11 | YSG | P23PM1027A_YSG | ok | [5 empty] | 0
ID-S01AP1020-00066 | 66 |  | P23PM1027A_HSH | pump PM1027A hydr.unit HU1009 - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 14 | 30 | DO |  |  | 0 | 11.1.1 | PM1027A hydr.unit HU1009 - start/stop |  | PM1027A | P23 | PM | 1027 | A | _ | 11 | HSH | P23PM1027A_HSH | ok | [5 empty] | 0
ID-S01AP1020-00067 | 67 |  | P23PM1027B_YLRE | pump PM1027B hydr.unit HU1009 - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 7 | 20 | DI |  |  | 0 | 11.1.2 | PM1027B hydr.unit HU1009 - in remote |  | PM1027B | P23 | PM | 1027 | B | _ | 11 | YLRE | P23PM1027B_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00068 | 68 |  | P23PM1027B_YLH | pump PM1027B hydr.unit HU1009 - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 8 | 20 | DI |  |  | 0 | 11.1.2 | PM1027B hydr.unit HU1009 - in running |  | PM1027B | P23 | PM | 1027 | B | _ | 11 | YLH | P23PM1027B_YLH | ok | [5 empty] | 0
ID-S01AP1020-00069 | 69 |  | P23PM1027B_YSG | pump PM1027B hydr.unit HU1009 - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 | B | 11.1.2.8 | 9 | 20 | DI |  |  | 0 | 11.1.2 | PM1027B hydr.unit HU1009 - supply fault |  | PM1027B | P23 | PM | 1027 | B | _ | 11 | YSG | P23PM1027B_YSG | ok | [5 empty] | 0
ID-S01AP1020-00070 | 70 |  | P23PM1027B_HSH | pump PM1027B hydr.unit HU1009 - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 15 | 30 | DO |  |  | 0 | 11.1.1 | PM1027B hydr.unit HU1009 - start/stop |  | PM1027B | P23 | PM | 1027 | B | _ | 11 | HSH | P23PM1027B_HSH | ok | [5 empty] | 0
ID-S01AP1020-00071 | 71 |  | P23FN1013B_YLRE | fan FN1013B hydr.unit HU1009 - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 10 | 20 | DI |  |  | 0 | 11.1.2 | FN1013B hydr.unit HU1009 - in remote |  | FN1013B | P23 | FN | 1013 | B | _ | 11 | YLRE | P23FN1013B_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00072 | 72 |  | P23FN1013B_YLH | fan FN1013B hydr.unit HU1009 - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 11 | 20 | DI |  |  | 0 | 11.1.2 | FN1013B hydr.unit HU1009 - in running |  | FN1013B | P23 | FN | 1013 | B | _ | 11 | YLH | P23FN1013B_YLH | ok | [5 empty] | 0
ID-S01AP1020-00073 | 73 |  | P23FN1013B_YSG | fan FN1013B hydr.unit HU1009 - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 | B | 11.1.2.8 | 12 | 20 | DI |  |  | 0 | 11.1.2 | FN1013B hydr.unit HU1009 - supply fault |  | FN1013B | P23 | FN | 1013 | B | _ | 11 | YSG | P23FN1013B_YSG | ok | [5 empty] | 0
ID-S01AP1020-00074 | 74 |  | P23FN1013B_HSH | fan FN1013B hydr.unit HU1009 - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 16 | 30 | DO |  |  | 0 | 11.1.1 | FN1013B hydr.unit HU1009 - start/stop |  | FN1013B | P23 | FN | 1013 | B | _ | 11 | HSH | P23FN1013B_HSH | ok | [5 empty] | 0
ID-S01AP1020-00075 | 75 |  | P23BR1020_HSK | burner BR1020 - trip |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DOS | RELAY | false | = | active | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | BR1020 - trip |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | HSK | P23BR1020_HSK | ok | [5 empty] | 0
ID-S01AP1020-00076 | 76 | P23BR1020_YSA | P23BR1020_YSA-1 | burner BR1020 - emergency |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DO | RELAY | false | = | active | 0 |  | 11 |  | 11.1.1.4 | 17 | 30 | DO |  |  | 0 | 11.1.1 | BR1020 - emergency |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | YSA-1 | P23BR1020_YSA-1 | ok | [5 empty] | 0
ID-S01AP1020-00077 | 77 |  | P23BR1020_HSH | burner BR1020 - burner start-stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DO | RELAY | true | = | start | 0 |  | 11 |  | 11.1.1.4 | 18 | 30 | DO |  |  | 0 | 11.1.1 | BR1020 - burner start-stop |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | HSH | P23BR1020_HSH | ok | [5 empty] | 0
ID-S01AP1020-00078 | 78 | P23BR1020_HS | P23BR1020_HS-1 | burner BR1020 - stand by |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DO | RELAY | true | = | standby | 0 |  | 11 |  | 11.1.1.4 | 19 | 30 | DO |  |  | 0 | 11.1.1 | BR1020 - stand by |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | HS-1 | P23BR1020_HS-1 | ok | [5 empty] | 0
ID-S01AP1020-00079 | 79 | P23BR1020_HS | P23BR1020_HS-2 | burner BR1020 - combust. select. |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DO | RELAY | true | = | liquid | 0 |  | 11 |  | 11.1.1.4 | 20 | 30 | DO |  |  | 0 | 11.1.1 | BR1020 - combust. select. |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | HS-2 | P23BR1020_HS-2 | ok | [5 empty] | 0
ID-S01AP1020-00080 | 80 | P23BR1020_HS | P23BR1020_HS-3 | burner BR1020 - perm. burn liq. waste |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DO | RELAY | true | = | permissive | 0 |  | 11 |  | 11.1.1.4 | 21 | 30 | DO |  |  | 0 | 11.1.1 | BR1020 - perm. burn liq. waste |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | HS-3 | P23BR1020_HS-3 | ok | [5 empty] | 0
ID-S01AP1020-00081 | 81 |  | P23BR1020_YL | burner BR1020 - burner vent. run |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DO | RELAY | true | = | run | 0 |  | 11 |  | 11.1.1.4 | 22 | 30 | DO |  |  | 0 | 11.1.1 | BR1020 - burner vent. run |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | YL | P23BR1020_YL | ok | [5 empty] | 0
ID-S01AP1020-00082 | 82 |  | P23BR1020_YLRE | burner BR1020 - burner in rem |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DI | SPST | true | → | remote | 0 |  | 11 |  | 11.1.1.3 | 25 | 32 | DI |  |  | 0 | 11.1.1 | BR1020 - burner in rem |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | YLRE | P23BR1020_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00083 | 83 |  | P23BR1020_YLH | burner BR1020 - burner ON |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DI | SPST | true | → | run | 0 |  | 11 |  | 11.1.1.3 | 26 | 32 | DI |  |  | 0 | 11.1.1 | BR1020 - burner ON |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | YLH | P23BR1020_YLH | ok | [5 empty] | 0
ID-S01AP1020-00084 | 84 | P23BR1020_YSA | P23BR1020_YSA-2 | burner BR1020 - common warning |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DI | SPST | false | → | active | 0 |  | 11 |  | 11.1.1.3 | 27 | 32 | DI |  |  | 0 | 11.1.1 | BR1020 - common warning |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | YSA-2 | P23BR1020_YSA-2 | ok | [5 empty] | 0
ID-S01AP1020-00085 | 85 |  | P23BR1020_YST | burner BR1020 - commnon trips |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DI | SPST | false | → | active | 0 |  | 11 |  | 11.1.1.3 | 28 | 32 | DI |  |  | 0 | 11.1.1 | BR1020 - commnon trips |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | YST | P23BR1020_YST | ok | [5 empty] | 0
ID-S01AP1020-00086 | 86 |  | P23BR1020_YSE | burner BR1020 - emergency pressed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | DI | SPST | false | → | pressed | 0 |  | 11 |  | 11.1.1.3 | 29 | 32 | DI |  |  | 0 | 11.1.1 | BR1020 - emergency pressed |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | YSE | P23BR1020_YSE | ok | [5 empty] | 0
ID-S01AP1020-00087 | 87 |  | P23BR1020_JY | burner BR1020 - load req. |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | AO | 4/20 mA | 0 | ∕ | 0...100 | % |  | 11 |  | 11.1.1.8 | 5 | 8 | AO |  |  | 0 | 11.1.1 | BR1020 - load req. |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | JY | P23BR1020_JY | ok |  |  |  | 0 |  | %
ID-S01AP1020-00088 | 88 | P23BR1020_FY | P23BR1020_FY-1 | burner BR1020 - liq. LH flow req. |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | AO | 4/20 mA | 0 | ∕ | 0...200 | kg/h |  | 11 |  | 11.1.1.8 | 6 | 8 | AO |  |  | 0 | 11.1.1 | BR1020 - liq. LH flow req. |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | FY-1 | P23BR1020_FY-1 | ok |  |  |  | 0 |  | kg/h
ID-S01AP1020-00089 | 89 | P23BR1020_FY | P23BR1020_FY-2 | burner BR1020 - visc. liq. flow req. | 57 |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | AO | 4/20 mA | 0 | ∕ | 0…500 | kg/h |  | 11 |  | 11.1.1.8 | 7 | 8 | AO |  |  | 0 | 11.1.1 | BR1020 - visc. liq. flow req. |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | FY-2 | P23BR1020_FY-2 | ok |  |  |  | 0 |  | kg/h
ID-S01AP1020-00090 | 90 | P23BR1020_JI | P23BR1020_JI-1 | burner BR1020 - load |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | AI | 4/20 mA | 0 | ∕ | 0...100 | % |  | 11 |  | 11.1.1.7 | 9 | 13 | AI |  |  | 0 | 11.1.1 | BR1020 - load |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | JI-1 | P23BR1020_JI-1 | ok |  |  |  | 0 | 0...100 | %
ID-S01AP1020-00091 | 91 | P23BR1020_JI | P23BR1020_JI-2 | burner BR1020 - liq. LH flow |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | AI | 4/20 mA | 0 | ∕ | 0...200 | kg/h |  | 11 |  | 11.1.1.7 | 10 | 13 | AI |  |  | 0 | 11.1.1 | BR1020 - liq. LH flow |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | JI-2 | P23BR1020_JI-2 | ok |  |  |  | 0 | 0...200 | kg/h
ID-S01AP1020-00092 | 92 | P23BR1020_JI | P23BR1020_JI-3 | burner BR1020 - visc. liq. flow |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_8 |  | AI | 4/20 mA | 0 | ∕ | 0…500 | kg/h |  | 11 |  | 11.1.1.7 | 11 | 13 | AI |  |  | 0 | 11.1.1 | BR1020 - visc. liq. flow |  | BR1020 | P23 | BR | 1020 |  | _ | 10 | JI-3 | P23BR1020_JI-3 | ok |  |  |  | 0 | 0…500 | kg/h
ID-S01AP1020-00093 | 93 |  | P23FN1021_YLRE | fan FN1021 burner BR1020 - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 30 | 32 | DI |  |  | 0 | 11.1.1 | FN1021 burner BR1020 - in remote |  | FN1021 | P23 | FN | 1021 |  | _ | 10 | YLRE | P23FN1021_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00094 | 94 |  | P23FN1021_YLH | fan FN1021 burner BR1020 - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.1.3 | 31 | 32 | DI |  |  | 0 | 11.1.1 | FN1021 burner BR1020 - in running |  | FN1021 | P23 | FN | 1021 |  | _ | 10 | YLH | P23FN1021_YLH | ok | [5 empty] | 0
ID-S01AP1020-00095 | 95 |  | P23FN1021_YSG | fan FN1021 burner BR1020 - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.1.3 | 32 | 32 | DI |  |  | 0 | 11.1.1 | FN1021 burner BR1020 - supply fault |  | FN1021 | P23 | FN | 1021 |  | _ | 10 | YSG | P23FN1021_YSG | ok | [5 empty] | 0
ID-S01AP1020-00096 | 96 |  | P23FN1021_HSH | fan FN1021 burner BR1020 - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 23 | 30 | DO |  |  | 0 | 11.1.1 | FN1021 burner BR1020 - start/stop |  | FN1021 | P23 | FN | 1021 |  | _ | 10 | HSH | P23FN1021_HSH | ok | [5 empty] | 0
ID-S01AP1020-00097 | 97 |  | P23FN1021_HSK | fan FN1021 burner BR1020 - interlock |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSK | DOS | RELAY | false | → | interlock | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | FN1021 burner BR1020 - interlock |  | FN1021 | P23 | FN | 1021 |  | _ | 10 | HSK | P23FN1021_HSK | ok | [5 empty] | 0
ID-S01AP1020-00098 | 98 |  | P23FN1025A_YLRE | fan FN1025A burner BR1024A - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.1.1 | 10 | 17 | DI |  |  | 0 | 11.1.1 | FN1025A burner BR1024A - in remote |  | FN1025A | P23 | FN | 1025 | A | _ | 11 | YLRE | P23FN1025A_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00099 | 99 |  | P23FN1025A_YLH | fan FN1025A burner BR1024A - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.1.1 | 11 | 17 | DI |  |  | 0 | 11.1.1 | FN1025A burner BR1024A - in running |  | FN1025A | P23 | FN | 1025 | A | _ | 11 | YLH | P23FN1025A_YLH | ok | [5 empty] | 0
ID-S01AP1020-00100 | 100 |  | P23FN1025A_YSG | fan FN1025A burner BR1024A - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 | A | 11.1.1.1 | 12 | 17 | DI |  |  | 0 | 11.1.1 | FN1025A burner BR1024A - supply fault |  | FN1025A | P23 | FN | 1025 | A | _ | 11 | YSG | P23FN1025A_YSG | ok | [5 empty] | 0
ID-S01AP1020-00101 | 101 |  | P23FN1025A_HSH | fan FN1025A burner BR1024A - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 24 | 30 | DO |  |  | 0 | 11.1.1 | FN1025A burner BR1024A - start/stop |  | FN1025A | P23 | FN | 1025 | A | _ | 11 | HSH | P23FN1025A_HSH | ok | [5 empty] | 0
ID-S01AP1020-00102 | 102 |  | P23FN1025A_HSK | fan FN1025A burner BR1024A - interlock |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSK | DOS | RELAY | false | → | interlock | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | FN1025A burner BR1024A - interlock |  | FN1025A | P23 | FN | 1025 | A | _ | 11 | HSK | P23FN1025A_HSK | ok | [5 empty] | 0
ID-S01AP1020-00103 | 103 |  | P23FN1025B_YLRE | fan FN1025B burner BR1024B - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 13 | 20 | DI |  |  | 0 | 11.1.2 | FN1025B burner BR1024B - in remote |  | FN1025B | P23 | FN | 1025 | B | _ | 11 | YLRE | P23FN1025B_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00104 | 104 |  | P23FN1025B_YLH | fan FN1025B burner BR1024B - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.2.8 | 14 | 20 | DI |  |  | 0 | 11.1.2 | FN1025B burner BR1024B - in running |  | FN1025B | P23 | FN | 1025 | B | _ | 11 | YLH | P23FN1025B_YLH | ok | [5 empty] | 0
ID-S01AP1020-00105 | 105 |  | P23FN1025B_YSG | fan FN1025B burner BR1024B - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 | B | 11.1.2.8 | 15 | 20 | DI |  |  | 0 | 11.1.2 | FN1025B burner BR1024B - supply fault |  | FN1025B | P23 | FN | 1025 | B | _ | 11 | YSG | P23FN1025B_YSG | ok | [5 empty] | 0
ID-S01AP1020-00106 | 106 |  | P23FN1025B_HSH | fan FN1025B burner BR1024B - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.1.4 | 25 | 30 | DO |  |  | 0 | 11.1.1 | FN1025B burner BR1024B - start/stop |  | FN1025B | P23 | FN | 1025 | B | _ | 11 | HSH | P23FN1025B_HSH | ok | [5 empty] | 0
ID-S01AP1020-00107 | 107 |  | P23FN1025B_HSK | fan FN1025B burner BR1024B - interlock |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSK | DOS | RELAY | false | → | interlock | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | FN1025B burner BR1024B - interlock |  | FN1025B | P23 | FN | 1025 | B | _ | 11 | HSK | P23FN1025B_HSK | ok | [5 empty] | 0
ID-S01AP1020-00108 | 108 |  | P23BR1024A_HSK | burner BR1024A - trip |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DOS | RELAY | false | = | active | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | BR1024A - trip |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | HSK | P23BR1024A_HSK | ok | [5 empty] | 0
ID-S01AP1020-00109 | 109 | P23BR1024A_YSA | P23BR1024A_YSA-1 | burner BR1024A - emergency |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | false | = | active | 0 |  | 11 |  | 11.1.1.4 | 26 | 30 | DO |  |  | 0 | 11.1.1 | BR1024A - emergency |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | YSA-1 | P23BR1024A_YSA-1 | ok | [5 empty] | 0
ID-S01AP1020-00110 | 110 |  | P23BR1024A_HSH | burner BR1024A - burner start-stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | start | 0 |  | 11 |  | 11.1.1.4 | 27 | 30 | DO |  |  | 0 | 11.1.1 | BR1024A - burner start-stop |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | HSH | P23BR1024A_HSH | ok | [5 empty] | 0
ID-S01AP1020-00111 | 111 | P23BR1024A_HS | P23BR1024A_HS-1 | burner BR1024A - stand by |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | standby | 0 |  | 11 |  | 11.1.1.4 | 28 | 30 | DO |  |  | 0 | 11.1.1 | BR1024A - stand by |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | HS-1 | P23BR1024A_HS-1 | ok | [5 empty] | 0
ID-S01AP1020-00112 | 112 | P23BR1024A_HS | P23BR1024A_HS-2 | burner BR1024A - combust. select. |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | liquid | 0 |  | 11 |  | 11.1.1.4 | 29 | 30 | DO |  |  | 0 | 11.1.1 | BR1024A - combust. select. |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | HS-2 | P23BR1024A_HS-2 | ok | [5 empty] | 0
ID-S01AP1020-00113 | 113 | P23BR1024A_HS | P23BR1024A_HS-3 | burner BR1024A - perm. burn liq. waste |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | permissive | 0 |  | 11 |  | 11.1.1.4 | 30 | 30 | DO |  |  | 0 | 11.1.1 | BR1024A - perm. burn liq. waste |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | HS-3 | P23BR1024A_HS-3 | ok | [5 empty] | 0
ID-S01AP1020-00114 | 114 |  | P23BR1024A_YL | burner BR1024A - burner vent. run |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | run | 0 |  | 11 |  | 11.1.2.5 | 1 | 30 | DO |  |  | 0 | 11.1.2 | BR1024A - burner vent. run |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | YL | P23BR1024A_YL | ok | [5 empty] | 0
ID-S01AP1020-00115 | 115 |  | P23BR1024A_YLRE | burner BR1024A - burner in rem |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | true | → | remote | 0 |  | 11 | A | 11.1.1.1 | 13 | 17 | DI |  |  | 0 | 11.1.1 | BR1024A - burner in rem |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | YLRE | P23BR1024A_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00116 | 116 |  | P23BR1024A_YLH | burner BR1024A - burner ON |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | true | → | run | 0 |  | 11 | A | 11.1.1.1 | 14 | 17 | DI |  |  | 0 | 11.1.1 | BR1024A - burner ON |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | YLH | P23BR1024A_YLH | ok | [5 empty] | 0
ID-S01AP1020-00117 | 117 | P23BR1024A_YSA | P23BR1024A_YSA-2 | burner BR1024A - common warning |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | false | → | active | 0 |  | 11 | A | 11.1.1.1 | 15 | 17 | DI |  |  | 0 | 11.1.1 | BR1024A - common warning |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | YSA-2 | P23BR1024A_YSA-2 | ok | [5 empty] | 0
ID-S01AP1020-00118 | 118 |  | P23BR1024A_YST | burner BR1024A - commnon trips |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | false | → | active | 0 |  | 11 | A | 11.1.1.1 | 16 | 17 | DI |  |  | 0 | 11.1.1 | BR1024A - commnon trips |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | YST | P23BR1024A_YST | ok | [5 empty] | 0
ID-S01AP1020-00119 | 119 |  | P23BR1024A_YSE | burner BR1024A - emergency pressed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | false | → | pressed | 0 |  | 11 | A | 11.1.1.1 | 17 | 17 | DI |  |  | 0 | 11.1.1 | BR1024A - emergency pressed |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | YSE | P23BR1024A_YSE | ok | [5 empty] | 0
ID-S01AP1020-00120 | 120 |  | P23BR1024A_JY | burner BR1024A - load req. |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | AO | 4/20 mA | 0 | ∕ | 0...100 | % |  | 11 |  | 11.1.1.8 | 8 | 8 | AO |  |  | 0 | 11.1.1 | BR1024A - load req. |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | JY | P23BR1024A_JY | ok |  |  |  | 0 |  | %
ID-S01AP1020-00121 | 121 |  | P23BR1024A_JI | burner BR1024A - load |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | AI | 4/20 mA | 0 | ∕ | 0...100 | % |  | 11 |  | 11.1.1.7 | 12 | 13 | AI |  |  | 0 | 11.1.1 | BR1024A - load |  | BR1024A | P23 | BR | 1024 | A | _ | 11 | JI | P23BR1024A_JI | ok |  |  |  | 0 | 0...100 | %
ID-S01AP1020-00122 | 122 |  | P23BR1024B_HSK | burner BR1024B - trip |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DOS | RELAY | false | = | active | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | BR1024B - trip |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | HSK | P23BR1024B_HSK | ok | [5 empty] | 0
ID-S01AP1020-00123 | 123 | P23BR1024B_YSA | P23BR1024B_YSA-1 | burner BR1024B - emergency |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | false | = | active | 0 |  | 11 |  | 11.1.2.5 | 2 | 30 | DO |  |  | 0 | 11.1.2 | BR1024B - emergency |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | YSA-1 | P23BR1024B_YSA-1 | ok | [5 empty] | 0
ID-S01AP1020-00124 | 124 |  | P23BR1024B_HSH | burner BR1024B - burner start-stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | start | 0 |  | 11 |  | 11.1.2.5 | 3 | 30 | DO |  |  | 0 | 11.1.2 | BR1024B - burner start-stop |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | HSH | P23BR1024B_HSH | ok | [5 empty] | 0
ID-S01AP1020-00125 | 125 | P23BR1024B_HS | P23BR1024B_HS-1 | burner BR1024B - stand by |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | standby | 0 |  | 11 |  | 11.1.2.5 | 4 | 30 | DO |  |  | 0 | 11.1.2 | BR1024B - stand by |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | HS-1 | P23BR1024B_HS-1 | ok | [5 empty] | 0
ID-S01AP1020-00126 | 126 | P23BR1024B_HS | P23BR1024B_HS-2 | burner BR1024B - combust. select. |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | liquid | 0 |  | 11 |  | 11.1.2.5 | 5 | 30 | DO |  |  | 0 | 11.1.2 | BR1024B - combust. select. |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | HS-2 | P23BR1024B_HS-2 | ok | [5 empty] | 0
ID-S01AP1020-00127 | 127 | P23BR1024B_HS | P23BR1024B_HS-3 | burner BR1024B - perm. burn liq. waste |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | permissive | 0 |  | 11 |  | 11.1.2.5 | 6 | 30 | DO |  |  | 0 | 11.1.2 | BR1024B - perm. burn liq. waste |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | HS-3 | P23BR1024B_HS-3 | ok | [5 empty] | 0
ID-S01AP1020-00128 | 128 |  | P23BR1024B_YL | burner BR1024B - burner vent. run |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DO | RELAY | true | = | run | 0 |  | 11 |  | 11.1.2.5 | 7 | 30 | DO |  |  | 0 | 11.1.2 | BR1024B - burner vent. run |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | YL | P23BR1024B_YL | ok | [5 empty] | 0
ID-S01AP1020-00129 | 129 |  | P23BR1024B_YLRE | burner BR1024B - burner in rem |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | true | → | remote | 0 |  | 11 | B | 11.1.2.8 | 16 | 20 | DI |  |  | 0 | 11.1.2 | BR1024B - burner in rem |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | YLRE | P23BR1024B_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00130 | 130 |  | P23BR1024B_YLH | burner BR1024B - burner ON |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | true | → | run | 0 |  | 11 | B | 11.1.2.8 | 17 | 20 | DI |  |  | 0 | 11.1.2 | BR1024B - burner ON |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | YLH | P23BR1024B_YLH | ok | [5 empty] | 0
ID-S01AP1020-00131 | 131 | P23BR1024B_YSA | P23BR1024B_YSA-2 | burner BR1024B - common warning |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | false | → | active | 0 |  | 11 | B | 11.1.2.8 | 18 | 20 | DI |  |  | 0 | 11.1.2 | BR1024B - common warning |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | YSA-2 | P23BR1024B_YSA-2 | ok | [5 empty] | 0
ID-S01AP1020-00132 | 132 |  | P23BR1024B_YST | burner BR1024B - commnon trips |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | false | → | active | 0 |  | 11 | B | 11.1.2.8 | 19 | 20 | DI |  |  | 0 | 11.1.2 | BR1024B - commnon trips |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | YST | P23BR1024B_YST | ok | [5 empty] | 0
ID-S01AP1020-00133 | 133 |  | P23BR1024B_YSE | burner BR1024B - emergency pressed |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | DI | SPST | false | → | pressed | 0 |  | 11 | B | 11.1.2.8 | 20 | 20 | DI |  |  | 0 | 11.1.2 | BR1024B - emergency pressed |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | YSE | P23BR1024B_YSE | ok | [5 empty] | 0
ID-S01AP1020-00134 | 134 |  | P23BR1024B_JY | burner BR1024B - load req. |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | AO | 4/20 mA | 0 | ∕ | 0...100 | % |  | 11 |  | 11.1.2.1 | 1 | 6 | AO |  |  | 0 | 11.1.2 | BR1024B - load req. |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | JY | P23BR1024B_JY | ok |  |  |  | 0 |  | %
ID-S01AP1020-00135 | 135 |  | P23BR1024B_JI | burner BR1024B - load |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | OPS_9 |  | AI | 4/20 mA | 0 | ∕ | 0...100 | % |  | 11 |  | 11.1.1.7 | 13 | 13 | AI |  |  | 0 | 11.1.1 | BR1024B - load |  | BR1024B | P23 | BR | 1024 | B | _ | 11 | JI | P23BR1024B_JI | ok |  |  |  | 0 | 0...100 | %
ID-S01AP1020-00136 | 136 |  | P23CY1019_YLRE | conveyor CY1019 was.comb. - in remote |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLRE | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 1 | 22 | DI |  |  | 0 | 11.1.2 | CY1019 was.comb. - in remote |  | CY1019 | P23 | CY | 1019 |  | _ | 10 | YLRE | P23CY1019_YLRE | ok | [5 empty] | 0
ID-S01AP1020-00137 | 137 |  | P23CY1019_YLH | conveyor CY1019 was.comb. - in running |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YLH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 2 | 22 | DI |  |  | 0 | 11.1.2 | CY1019 was.comb. - in running |  | CY1019 | P23 | CY | 1019 |  | _ | 10 | YLH | P23CY1019_YLH | ok | [5 empty] | 0
ID-S01AP1020-00138 | 138 |  | P23CY1019_YSG | conveyor CY1019 was.comb. - supply fault |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | YSG | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 3 | 22 | DI |  |  | 0 | 11.1.2 | CY1019 was.comb. - supply fault |  | CY1019 | P23 | CY | 1019 |  | _ | 10 | YSG | P23CY1019_YSG | ok | [5 empty] | 0
ID-S01AP1020-00139 | 139 |  | P23CY1019_HSH | conveyor CY1019 was.comb. - start/stop |  |  | ROT.KILN ST.GEN. 1 |  | P23MCC0001 |  | S01AP1020 |  |  | EM_112 | HSH | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 8 | 30 | DO |  |  | 0 | 11.1.2 | CY1019 was.comb. - start/stop |  | CY1019 | P23 | CY | 1019 |  | _ | 10 | HSH | P23CY1019_HSH | ok | [5 empty] | 0
ID-S01AP1020-00140 | 140 |  | P23FI1011 | flow FT1011 ve.air distr. FN1017 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1001 |  | S01AP1020 |  |  | SG_T2 | FT | AIS | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | FT1011 ve.air distr. FN1017 |  | FT1011 | P23 | FI | 1011 |  |  |  |  | P23FI1011 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00141 | 141 |  | P23FI1012 | flow FT1012 was.comb. cool.wat. |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1001 |  | S01AP1020 |  |  | SG_T4 | FT | AI | 4/20 mA - 4W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 1 | 15 | AI |  |  | 0 | 11.1.2 | FT1012 was.comb. cool.wat. |  | FT1012 | P23 | FI | 1012 |  |  |  |  | P23FI1012 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00142 | 142 |  | P23FI1013 | flow FT1013 was.comb. cool.wat. from pumps |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1001 |  | S01AP1020 |  |  | SG_T4 | FT | AIS | 4/20 mA - 4W | xxx | ∕ | xxx | xxx |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | FT1013 was.comb. cool.wat. from pumps |  | FT1013 | P23 | FI | 1013 |  |  |  |  | P23FI1013 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00143 | 143 |  | P23PI1011 | press. PT1011 ve.air distr. FN1017 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1001 |  | S01AP1020 |  |  | SG_T2 | PT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 2 | 15 | AI |  |  | 0 | 11.1.2 | PT1011 ve.air distr. FN1017 |  | PT1011 | P23 | PI | 1011 |  |  |  |  | P23PI1011 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00144 | 144 |  | P23PI1013 | press. PT1013 ve.air distr. FN1018 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1002 |  | S01AP1020 |  |  | SG_T2 | PT | AIS | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | PT1013 ve.air distr. FN1018 |  | PT1013 | P23 | PI | 1013 |  |  |  |  | P23PI1013 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00145 | 145 |  | P23PI1015 | press. PT1015 ve.air distr. FN1021 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1001 |  | S01AP1020 |  |  | SG_T2 | PT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 3 | 15 | AI |  |  | 0 | 11.1.2 | PT1015 ve.air distr. FN1021 |  | PT1015 | P23 | PI | 1015 |  |  |  |  | P23PI1015 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00146 | 146 |  | P23SI1011 | speed ST1011 rot.kiln RK1001 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1002 |  | S01AP1020 |  |  | SG_T4 | ST | AI | 4/20 mA - 4W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 4 | 15 | AI |  |  | 0 | 11.1.2 | ST1011 rot.kiln RK1001 |  | ST1011 | P23 | SI | 1011 |  |  |  |  | P23SI1011 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00147 | 147 |  | P23YL1012 | speed L SSL1012 conveyor CY1003 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBD1001 |  | S01AP1020 |  |  | SG_YL | YL | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 4 | 22 | DI |  |  | 0 | 11.1.2 | L SSL1012 conveyor CY1003 |  | L | P23 | YL | 1012 |  |  |  |  | P23YL1012 | ok | [5 empty] | 0
ID-S01AP1020-00148 | 148 |  | P23FV1011_ZSH | vlv. FV1011 was.comb. - opened |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | ZSH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 5 | 22 | DI |  |  | 0 | 11.1.2 | FV1011 was.comb. - opened |  | FV1011 | P23 | FV | 1011 |  | _ | 10 | ZSH | P23FV1011_ZSH | ok | [5 empty] | 0
ID-S01AP1020-00149 | 149 |  | P23FV1011_ZSL | vlv. FV1011 was.comb. - closed |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | ZSL | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 6 | 22 | DI |  |  | 0 | 11.1.2 | FV1011 was.comb. - closed |  | FV1011 | P23 | FV | 1011 |  | _ | 10 | ZSL | P23FV1011_ZSL | ok | [5 empty] | 0
ID-S01AP1020-00150 | 150 |  | P23FV1011_HSK | vlv. FV1011 was.comb. - interlock |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | HSK | DO | RELAY - 24 Vac | false | → | active | 0 |  | 11 |  | 11.1.3.4 | 1 | 32 | DO |  |  | 0 | 11.1.3 | FV1011 was.comb. - interlock |  | FV1011 | P23 | FV | 1011 |  | _ | 10 | HSK | P23FV1011_HSK | ok | [5 empty] | 0
ID-S01AP1020-00151 | 151 |  | P23FV1011_ZI | vlv. FV1011 was.comb. - position |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | ZT | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.2.2 | 5 | 15 | AI |  |  | 0 | 11.1.2 | FV1011 was.comb. - position |  | FV1011 | P23 | FV | 1011 |  | _ | 10 | ZI | P23FV1011_ZI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-00152 | 152 |  | P23FV1011_ZY | vlv. FV1011 was.comb. - req.pos. |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | ZY | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.3.8 | 1 | 6 | AO |  |  | 0 | 11.1.3 | FV1011 was.comb. - req.pos. |  | FV1011 | P23 | FV | 1011 |  | _ | 10 | ZY | P23FV1011_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1020-00153 | 153 |  | P23HCV1011_ZSH | man.contr.vlv. HCV1011 steam from LP Header - opened |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | ZSH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 7 | 22 | DI |  |  | 0 | 11.1.2 | HCV1011 steam from LP Header - opened |  | HCV1011 | P23 | HCV | 1011 |  | _ | 11 | ZSH | P23HCV1011_ZSH | ok | [5 empty] | 0
ID-S01AP1020-00154 | 154 |  | P23HCV1011_ZSL | man.contr.vlv. HCV1011 steam from LP Header - closed |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | ZSL | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 8 | 22 | DI |  |  | 0 | 11.1.2 | HCV1011 steam from LP Header - closed |  | HCV1011 | P23 | HCV | 1011 |  | _ | 11 | ZSL | P23HCV1011_ZSL | ok | [5 empty] | 0
ID-S01AP1020-00155 | 155 |  | P23HCV1011_HSK | man.contr.vlv. HCV1011 steam from LP Header - interlock |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | HSK | DOS | RELAY - 24 Vac | false | → | active | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | HCV1011 steam from LP Header - interlock |  | HCV1011 | P23 | HCV | 1011 |  | _ | 11 | HSK | P23HCV1011_HSK | ok | [5 empty] | 0
ID-S01AP1020-00156 | 156 |  | P23HCV1011_ZI | man.contr.vlv. HCV1011 steam from LP Header - position |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | ZT | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.2.2 | 6 | 15 | AI |  |  | 0 | 11.1.2 | HCV1011 steam from LP Header - position |  | HCV1011 | P23 | HCV | 1011 |  | _ | 11 | ZI | P23HCV1011_ZI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-00157 | 157 |  | P23HCV1011_ZY | man.contr.vlv. HCV1011 steam from LP Header - req.pos. |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_CV | ZY | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.3.8 | 2 | 6 | AO |  |  | 0 | 11.1.3 | HCV1011 steam from LP Header - req.pos. |  | HCV1011 | P23 | HCV | 1011 |  | _ | 11 | ZY | P23HCV1011_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1020-00158 | 158 |  | P23TI1011 | temp. TT1011 rot.kiln driving unit |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1001 |  | S01AP1020 |  |  | SG_T2 | TT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 7 | 15 | AI |  |  | 0 | 11.1.2 | TT1011 rot.kiln driving unit |  | TT1011 | P23 | TI | 1011 |  |  |  |  | P23TI1011 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00159 | 159 |  | P23TI1012 | temp. TT1012 rot.kiln driving unit |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1001 |  | S01AP1020 |  |  | SG_T2 | TT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 8 | 15 | AI |  |  | 0 | 11.1.2 | TT1012 rot.kiln driving unit |  | TT1012 | P23 | TI | 1012 |  |  |  |  | P23TI1012 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00160 | 160 |  | P23TI1013 | temp. TT1013 rot.kiln RK1001 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1002 |  | S01AP1020 |  |  | SG_T2 | TT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 9 | 15 | AI |  |  | 0 | 11.1.2 | TT1013 rot.kiln RK1001 |  | TT1013 | P23 | TI | 1013 |  |  |  |  | P23TI1013 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00161 | 161 |  | P23YL1016 | pos. L ZSL1016 rot.kiln driving unit |  |  | ROT.KILN ST.GEN. 1 |  | P23JBD1001 |  | S01AP1020 |  |  | SG_YL | YL | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 9 | 22 | DI |  |  | 0 | 11.1.2 | L ZSL1016 rot.kiln driving unit |  | L | P23 | YL | 1016 |  |  |  |  | P23YL1016 | ok | [5 empty] | 0
ID-S01AP1020-00162 | 162 |  | P23FI1002 | flow FT1002 cool.wat. |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1003 |  | S01AP1020 |  |  | SG_T2 | FT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 10 | 15 | AI |  |  | 0 | 11.1.2 | FT1002 cool.wat. |  | FT1002 | P23 | FI | 1002 |  |  |  |  | P23FI1002 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00163 | 163 |  | P23FI1003 | flow FT1003 cool.wat. |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1003 |  | S01AP1020 |  |  | SG_T2 | FT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 11 | 15 | AI |  |  | 0 | 11.1.2 | FT1003 cool.wat. |  | FT1003 | P23 | FI | 1003 |  |  |  |  | P23FI1003 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00164 | 164 |  | P23MOV1001_ZSH | vlv. MOV1001 wat. to conveyor CY1019 - opened |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_2P | ZSH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 10 | 22 | DI |  |  | 0 | 11.1.2 | MOV1001 wat. to conveyor CY1019 - opened |  | MOV1001 | P23 | MOV | 1001 |  | _ | 11 | ZSH | P23MOV1001_ZSH | ok | [5 empty] | 0
ID-S01AP1020-00165 | 165 |  | P23MOV1001_ZSL | vlv. MOV1001 wat. to conveyor CY1019 - closed |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_2P | ZSL | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 11 | 22 | DI |  |  | 0 | 11.1.2 | MOV1001 wat. to conveyor CY1019 - closed |  | MOV1001 | P23 | MOV | 1001 |  | _ | 11 | ZSL | P23MOV1001_ZSL | ok | [5 empty] | 0
ID-S01AP1020-00166 | 166 |  | P23MOV1001_HSH | vlv. MOV1001 wat. to conveyor CY1019 - open/close |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | PV_2P | HSH | DO | RELAY - 24 Vac | true | → | open | 0 |  | 11 |  | 11.1.3.4 | 2 | 32 | DO |  |  | 0 | 11.1.3 | MOV1001 wat. to conveyor CY1019 - open/close |  | MOV1001 | P23 | MOV | 1001 |  | _ | 11 | HSH | P23MOV1001_HSH | ok | [5 empty] | 0
ID-S01AP1020-00167 | 167 |  | P23PI1001 | press. PT1001 ve.air distr. FN1025/A |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1002 |  | S01AP1020 |  |  | SG_T2 | PT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 12 | 15 | AI |  |  | 0 | 11.1.2 | PT1001 ve.air distr. FN1025/A |  | PT1001 | P23 | PI | 1001 |  |  |  |  | P23PI1001 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00168 | 168 |  | P23PI1004 | press. PT1004 ve.air distr. FN1025/B |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1002 |  | S01AP1020 |  |  | SG_T2 | PT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 13 | 15 | AI |  |  | 0 | 11.1.2 | PT1004 ve.air distr. FN1025/B |  | PT1004 | P23 | PI | 1004 |  |  |  |  | P23PI1004 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00169 | 169 |  | P23PI1005A | press. PT1005A post com.chamber PCC1002 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1003 |  | S01AP1020 |  |  | SG_T2 | PT | AIS | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | PT1005A post com.chamber PCC1002 |  | PT1005A | P23 | PI | 1005 | A |  |  |  | P23PI1005A | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00170 | 170 |  | P23PI1005B | press. PT1005B post com.chamber PCC1002 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1003 |  | S01AP1020 |  |  | SG_T2 | PT | AIS | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | PT1005B post com.chamber PCC1002 |  | PT1005B | P23 | PI | 1005 | B |  |  |  | P23PI1005B | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00171 | 171 | P23YS1001 | P23YS1001-1 | speed L SSL1001 conveyor CY1019 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBD1002 |  | S01AP1020 |  |  | SG_YS | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 12 | 22 | DI |  |  | 0 | 11.1.2 | L SSL1001 conveyor CY1019 |  | L | P23 | YS | 1001 | - |  |  | 1 | P23YS1001-1 | ok | [5 empty] | 0
ID-S01AP1020-00172 | 172 |  | P23TI1001 | temp. TT1001 post com.chamber PCC1002 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1002 |  | S01AP1020 |  |  | SG_T2 | TT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 14 | 15 | AI |  |  | 0 | 11.1.2 | TT1001 post com.chamber PCC1002 |  | TT1001 | P23 | TI | 1001 |  |  |  |  | P23TI1001 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00173 | 173 |  | P23TI1002 | temp. TT1002 Opt. Pirometer |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1003 |  | S01AP1020 |  |  | SG_T4 | TT | AIS | 4/20 mA - 4W | xxx | ∕ | xxx | xxx |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | TT1002 Opt. Pirometer |  | TT1002 | P23 | TI | 1002 |  |  |  |  | P23TI1002 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00174 | 174 |  | P23TI1003 | temp. TT1003 Opt. Pirometer |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1003 |  | S01AP1020 |  |  | SG_T4 | TT | AIS | 4/20 mA - 4W | xxx | ∕ | xxx | xxx |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | TT1003 Opt. Pirometer |  | TT1003 | P23 | TI | 1003 |  |  |  |  | P23TI1003 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00175 | 175 |  | P23TI1004 | temp. TT1004 wat. conveyor CY1019 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBA1002 |  | S01AP1020 |  |  | SG_T2 | TT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.2.2 | 15 | 15 | AI |  |  | 0 | 11.1.2 | TT1004 wat. conveyor CY1019 |  | TT1004 | P23 | TI | 1004 |  |  |  |  | P23TI1004 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00176 | 176 | P23YS1001 | P23YS1001-2 | lev. L LSL1001 wat. conveyor CY1019 |  |  | ROT.KILN ST.GEN. 1 |  | P23JBD1002 |  | S01AP1020 |  |  | SG_YS | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 13 | 22 | DI |  |  | 0 | 11.1.2 | L LSL1001 wat. conveyor CY1019 |  | L | P23 | YS | 1001 | - |  |  | 2 | P23YS1001-2 | ok | [5 empty] | 0
ID-S01AP1020-00177 | 177 | P23YS1001 | P23YS1001-3 | lev. H LSH1001 wat. conveyor CY1019 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_YS | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 14 | 22 | DI |  |  | 0 | 11.1.2 | H LSH1001 wat. conveyor CY1019 |  | H | P23 | YS | 1001 | - |  |  | 3 | P23YS1001-3 | ok | [5 empty] | 0
ID-S01AP1020-00178 | 178 |  | P23CLV1001_ZSH | clapet vlv. CLV1001 stack SK1029 - opened |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | MV_CB | ZSH | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 15 | 22 | DI |  |  | 0 | 11.1.2 | vlv. CLV1001 stack SK1029 - opened |  | vlv. | P23 | CLV | 1001 |  | _ | 11 | ZSH | P23CLV1001_ZSH | ok | [5 empty] | 0
ID-S01AP1020-00179 | 179 |  | P23CLV1001_ZSL | clapet vlv. CLV1001 stack SK1029 - closed |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | MV_CB | ZSL | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.7 | 16 | 22 | DI |  |  | 0 | 11.1.2 | vlv. CLV1001 stack SK1029 - closed |  | vlv. | P23 | CLV | 1001 |  | _ | 11 | ZSL | P23CLV1001_ZSL | ok | [5 empty] | 0
ID-S01AP1020-00180 | 180 |  | P23CLV1001_HSK | clapet vlv. CLV1001 stack SK1029 - force open |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | MV_CB | HSK | DOS | RELAY - 24 Vac | false | = | open | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | vlv. CLV1001 stack SK1029 - force open |  | vlv. | P23 | CLV | 1001 |  | _ | 11 | HSK | P23CLV1001_HSK | ok | [5 empty] | 0
ID-S01AP1020-00181 | 181 |  | P23SOV1002_SOV | vlv. SOV1002 compr.air to TT1002 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 3 | 32 | DO |  |  | 0 | 11.1.3 | SOV1002 compr.air to TT1002 |  | SOV1002 | P23 | SOV | 1002 |  | _ | 11 | SOV | P23SOV1002_SOV | ok | [5 empty] | 0
ID-S01AP1020-00182 | 182 |  | P23SOV1003_SOV | vlv. SOV1003 compr.air to TT1003 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 4 | 32 | DO |  |  | 0 | 11.1.3 | SOV1003 compr.air to TT1003 |  | SOV1003 | P23 | SOV | 1003 |  | _ | 11 | SOV | P23SOV1003_SOV | ok | [5 empty] | 0
ID-S01AP1020-00183 | 183 |  | P23SOV1021_LI | lev. LT1021 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | LT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 1 | 14 | AI |  |  | 0 | 11.1.4 | LT1021 hydr.unit HU1009 |  | LT1021 | P23 | SOV | 1021 |  | _ | 11 | LI | P23SOV1021_LI | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00184 | 184 |  | P23LI1022 | loc.lev. LI1022 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | LI | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 2 | 14 | AI |  |  | 0 | 11.1.4 | LI1022 hydr.unit HU1009 |  | LI1022 | P23 | LI | 1022 |  |  |  |  | P23LI1022 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00185 | 185 |  | P23PI1021 | press. PT1021 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | PT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 3 | 14 | AI |  |  | 0 | 11.1.4 | PT1021 hydr.unit HU1009 |  | PT1021 | P23 | PI | 1021 |  |  |  |  | P23PI1021 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00186 | 186 |  | P23YS1023 | pres. L PSL1023 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_YS | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 17 | 22 | DI |  |  | 0 | 11.1.2 | L PSL1023 hydr.unit HU1009 |  | L | P23 | YS | 1023 |  |  |  |  | P23YS1023 | ok | [5 empty] | 0
ID-S01AP1020-00187 | 187 |  | P23YS1024 | pres. L PSL1024 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_YS | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 18 | 22 | DI |  |  | 0 | 11.1.2 | L PSL1024 hydr.unit HU1009 |  | L | P23 | YS | 1024 |  |  |  |  | P23YS1024 | ok | [5 empty] | 0
ID-S01AP1020-00188 | 188 |  | P23YS1025 | pres. L PSL1025 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_YS | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 19 | 22 | DI |  |  | 0 | 11.1.2 | L PSL1025 hydr.unit HU1009 |  | L | P23 | YS | 1025 |  |  |  |  | P23YS1025 | ok | [5 empty] | 0
ID-S01AP1020-00189 | 189 |  | P23YS1026 | pres. L PSL1026 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_YS | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 20 | 22 | DI |  |  | 0 | 11.1.2 | L PSL1026 hydr.unit HU1009 |  | L | P23 | YS | 1026 |  |  |  |  | P23YS1026 | ok | [5 empty] | 0
ID-S01AP1020-00190 | 190 |  | P23YS1027 | pres. L PSL1027 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_YS | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 21 | 22 | DI |  |  | 0 | 11.1.2 | L PSL1027 hydr.unit HU1009 |  | L | P23 | YS | 1027 |  |  |  |  | P23YS1027 | ok | [5 empty] | 0
ID-S01AP1020-00191 | 191 |  | P23PIT1030 | press. PIT1030 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | PIT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 4 | 14 | AI |  |  | 0 | 11.1.4 | PIT1030 hydr.unit HU1009 |  | PIT1030 | P23 | PIT | 1030 |  |  |  |  | P23PIT1030 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00192 | 192 |  | P23TIT1021 | temp. TIT1021 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | TIT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 5 | 14 | AI |  |  | 0 | 11.1.4 | TIT1021 hydr.unit HU1009 |  | TIT1021 | P23 | TIT | 1021 |  |  |  |  | P23TIT1021 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00193 | 193 |  | P23YS1022 | temp. H TSH1022 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_YS | YS | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.7 | 22 | 22 | DI |  |  | 0 | 11.1.2 | H TSH1022 hydr.unit HU1009 |  | H | P23 | YS | 1022 |  |  |  |  | P23YS1022 | ok | [5 empty] | 0
ID-S01AP1020-00194 | 194 |  | P23ZI1021 | Posit. ZT1021 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | ZT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 6 | 14 | AI |  |  | 0 | 11.1.4 | ZT1021 hydr.unit HU1009 |  | ZT1021 | P23 | ZI | 1021 |  |  |  |  | P23ZI1021 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00195 | 195 |  | P23ZI1022 | Posit. ZT1022 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | ZT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 7 | 14 | AI |  |  | 0 | 11.1.4 | ZT1022 hydr.unit HU1009 |  | ZT1022 | P23 | ZI | 1022 |  |  |  |  | P23ZI1022 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00196 | 196 |  | P23ZI1023 | Posit. ZT1023 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | ZT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 8 | 14 | AI |  |  | 0 | 11.1.4 | ZT1023 hydr.unit HU1009 |  | ZT1023 | P23 | ZI | 1023 |  |  |  |  | P23ZI1023 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00197 | 197 |  | P23ZI1024 | Posit. ZT1024 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | ZT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 9 | 14 | AI |  |  | 0 | 11.1.4 | ZT1024 hydr.unit HU1009 |  | ZT1024 | P23 | ZI | 1024 |  |  |  |  | P23ZI1024 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00198 | 198 |  | P23ZI1025 | Posit. ZT1025 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_T2 | ZT | AI | 4/20 mA - 2W | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.4.4 | 10 | 14 | AI |  |  | 0 | 11.1.4 | ZT1025 hydr.unit HU1009 |  | ZT1025 | P23 | ZI | 1025 |  |  |  |  | P23ZI1025 | ok |  |  |  | xxx | xxx | xxx
ID-S01AP1020-00199 | 199 |  | P23SOV1021_HSH | vlv. SOV1021 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 5 | 32 | DO |  |  | 0 | 11.1.3 | SOV1021 hydr.unit HU1009 |  | SOV1021 | P23 | SOV | 1021 |  | _ | 11 | HSH | P23SOV1021_HSH | ok | [5 empty] | 0
ID-S01AP1020-00200 | 200 |  | P23SOV1022_HSH | vlv. SOV1022 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 6 | 32 | DO |  |  | 0 | 11.1.3 | SOV1022 hydr.unit HU1009 |  | SOV1022 | P23 | SOV | 1022 |  | _ | 11 | HSH | P23SOV1022_HSH | ok | [5 empty] | 0
ID-S01AP1020-00201 | 201 |  | P23SOV1023_HSH | vlv. SOV1023 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 7 | 32 | DO |  |  | 0 | 11.1.3 | SOV1023 hydr.unit HU1009 |  | SOV1023 | P23 | SOV | 1023 |  | _ | 11 | HSH | P23SOV1023_HSH | ok | [5 empty] | 0
ID-S01AP1020-00202 | 202 |  | P23SOV1024_HSH | vlv. SOV1024 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 8 | 32 | DO |  |  | 0 | 11.1.3 | SOV1024 hydr.unit HU1009 |  | SOV1024 | P23 | SOV | 1024 |  | _ | 11 | HSH | P23SOV1024_HSH | ok | [5 empty] | 0
ID-S01AP1020-00203 | 203 |  | P23SOV1025_HSH | vlv. SOV1025 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 9 | 32 | DO |  |  | 0 | 11.1.3 | SOV1025 hydr.unit HU1009 |  | SOV1025 | P23 | SOV | 1025 |  | _ | 11 | HSH | P23SOV1025_HSH | ok | [5 empty] | 0
ID-S01AP1020-00204 | 204 |  | P23SOV1026_HSH | vlv. SOV1026 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 10 | 32 | DO |  |  | 0 | 11.1.3 | SOV1026 hydr.unit HU1009 |  | SOV1026 | P23 | SOV | 1026 |  | _ | 11 | HSH | P23SOV1026_HSH | ok | [5 empty] | 0
ID-S01AP1020-00205 | 205 |  | P23SOV1027_HSH | vlv. SOV1027 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 11 | 32 | DO |  |  | 0 | 11.1.3 | SOV1027 hydr.unit HU1009 |  | SOV1027 | P23 | SOV | 1027 |  | _ | 11 | HSH | P23SOV1027_HSH | ok | [5 empty] | 0
ID-S01AP1020-00206 | 206 |  | P23SOV1028_HSH | vlv. SOV1028 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 12 | 32 | DO |  |  | 0 | 11.1.3 | SOV1028 hydr.unit HU1009 |  | SOV1028 | P23 | SOV | 1028 |  | _ | 11 | HSH | P23SOV1028_HSH | ok | [5 empty] | 0
ID-S01AP1020-00207 | 207 |  | P23SOV1029_HSH | vlv. SOV1029 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 13 | 32 | DO |  |  | 0 | 11.1.3 | SOV1029 hydr.unit HU1009 |  | SOV1029 | P23 | SOV | 1029 |  | _ | 11 | HSH | P23SOV1029_HSH | ok | [5 empty] | 0
ID-S01AP1020-00208 | 208 |  | P23SOV1030_HSH | vlv. SOV1030 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 14 | 32 | DO |  |  | 0 | 11.1.3 | SOV1030 hydr.unit HU1009 |  | SOV1030 | P23 | SOV | 1030 |  | _ | 11 | HSH | P23SOV1030_HSH | ok | [5 empty] | 0
ID-S01AP1020-00209 | 209 |  | P23SOV1031_HSH | vlv. SOV1031 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 15 | 32 | DO |  |  | 0 | 11.1.3 | SOV1031 hydr.unit HU1009 |  | SOV1031 | P23 | SOV | 1031 |  | _ | 11 | HSH | P23SOV1031_HSH | ok | [5 empty] | 0
ID-S01AP1020-00210 | 210 |  | P23SOV1032_HSH | vlv. SOV1032 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 16 | 32 | DO |  |  | 0 | 11.1.3 | SOV1032 hydr.unit HU1009 |  | SOV1032 | P23 | SOV | 1032 |  | _ | 11 | HSH | P23SOV1032_HSH | ok | [5 empty] | 0
ID-S01AP1020-00211 | 211 |  | P23SOV1033_HSH | vlv. SOV1033 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 17 | 32 | DO |  |  | 0 | 11.1.3 | SOV1033 hydr.unit HU1009 |  | SOV1033 | P23 | SOV | 1033 |  | _ | 11 | HSH | P23SOV1033_HSH | ok | [5 empty] | 0
ID-S01AP1020-00212 | 212 |  | P23SOV1034_HSH | vlv. SOV1034 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 18 | 32 | DO |  |  | 0 | 11.1.3 | SOV1034 hydr.unit HU1009 |  | SOV1034 | P23 | SOV | 1034 |  | _ | 11 | HSH | P23SOV1034_HSH | ok | [5 empty] | 0
ID-S01AP1020-00213 | 213 |  | P23SOV1035_HSH | vlv. SOV1035 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 19 | 32 | DO |  |  | 0 | 11.1.3 | SOV1035 hydr.unit HU1009 |  | SOV1035 | P23 | SOV | 1035 |  | _ | 11 | HSH | P23SOV1035_HSH | ok | [5 empty] | 0
ID-S01AP1020-00214 | 214 |  | P23SOV1036_HSH | vlv. SOV1036 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 20 | 32 | DO |  |  | 0 | 11.1.3 | SOV1036 hydr.unit HU1009 |  | SOV1036 | P23 | SOV | 1036 |  | _ | 11 | HSH | P23SOV1036_HSH | ok | [5 empty] | 0
ID-S01AP1020-00215 | 215 |  | P23SOV1037_HSH | vlv. SOV1037 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 21 | 32 | DO |  |  | 0 | 11.1.3 | SOV1037 hydr.unit HU1009 |  | SOV1037 | P23 | SOV | 1037 |  | _ | 11 | HSH | P23SOV1037_HSH | ok | [5 empty] | 0
ID-S01AP1020-00216 | 216 |  | P23SOV1038_HSH | vlv. SOV1038 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 22 | 32 | DO |  |  | 0 | 11.1.3 | SOV1038 hydr.unit HU1009 |  | SOV1038 | P23 | SOV | 1038 |  | _ | 11 | HSH | P23SOV1038_HSH | ok | [5 empty] | 0
ID-S01AP1020-00217 | 217 |  | P23SOV1039_HSH | vlv. SOV1039 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 23 | 32 | DO |  |  | 0 | 11.1.3 | SOV1039 hydr.unit HU1009 |  | SOV1039 | P23 | SOV | 1039 |  | _ | 11 | HSH | P23SOV1039_HSH | ok | [5 empty] | 0
ID-S01AP1020-00218 | 218 |  | P23SOV1040A_HSH | vlv. SOV1040A hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 24 | 32 | DO |  |  | 0 | 11.1.3 | SOV1040A hydr.unit HU1009 |  | SOV1040A | P23 | SOV | 1040 | A | _ | 12 | HSH | P23SOV1040A_HSH | ok | [5 empty] | 0
ID-S01AP1020-00219 | 219 |  | P23SOV1040B_HSH | vlv. SOV1040B hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 25 | 32 | DO |  |  | 0 | 11.1.3 | SOV1040B hydr.unit HU1009 |  | SOV1040B | P23 | SOV | 1040 | B | _ | 12 | HSH | P23SOV1040B_HSH | ok | [5 empty] | 0
ID-S01AP1020-00220 | 220 |  | P23SOV1042_HSH | vlv. SOV1042 hydr.unit HU1009 |  |  | ROT.KILN ST.GEN. 1 |  |  |  | S01AP1020 |  |  | SG_HS | SOV | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 26 | 32 | DO |  |  | 0 | 11.1.3 | SOV1042 hydr.unit HU1009 |  | SOV1042 | P23 | SOV | 1042 |  | _ | 11 | HSH | P23SOV1042_HSH | ok | [5 empty] | 0
ID-S01AP1020-10001 | 1 |  | P29FI1205 | feed wat. - flow |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1006 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 20 | t/h |  | 11 |  | 11.1.3.7 | 1 | 15 | AI |  |  | 0 | 11.1.3 | wat. - flow |  | wat. | P29 | FI | 1205 |  |  |  |  | P29FI1205 | ok |  |  |  | 0 | 20 | t/h
ID-S01AP1020-10002 | 2 |  | P29TI1205 | feed wat. - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1205 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 300 | °C |  | 11 |  | 11.1.4.4 | 11 | 14 | AI |  |  | 0 | 11.1.4 | wat. - temp. |  | wat. | P29 | TI | 1205 |  |  |  |  | P29TI1205 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1020-10003 | 3 |  | P29PI1206 | feed wat. - press. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1005 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 50 | bar |  | 11 |  | 11.1.4.2 | 1 | 16 | AI |  |  | 0 | 11.1.4 | wat. - press. |  | wat. | P29 | PI | 1206 |  |  |  |  | P29PI1206 | ok |  |  |  | 0 | 50 | bar
ID-S01AP1020-10004 | 4 |  | P29FV1205_ZI | vlv. FV1205 feed wat. - position |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1007 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.3.7 | 2 | 15 | AI |  |  | 0 | 11.1.3 | FV1205 feed wat. - position |  | FV1205 | P29 | FV | 1205 |  | _ | 10 | ZI | P29FV1205_ZI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-10005 | 5 |  | P29FV1205_ZY | vlv. FV1205 feed wat. - req.pos. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1007 |  | S01AP1020 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.2.1 | 2 | 6 | AO |  |  | 0 | 11.1.2 | FV1205 feed wat. - req.pos. |  | FV1205 | P29 | FV | 1205 |  | _ | 10 | ZY | P29FV1205_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1020-10006 | 6 |  | P29FV1207_ZI | vlv. TV1207 feed wat. - position |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1007 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.3.7 | 3 | 15 | AI |  |  | 0 | 11.1.3 | TV1207 feed wat. - position |  | TV1207 | P29 | FV | 1207 |  | _ | 10 | ZI | P29FV1207_ZI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-10007 | 7 |  | P29FV1207_ZY | vlv. TV1207 feed wat. - req.pos. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1007 |  | S01AP1020 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.2.1 | 3 | 6 | AO |  |  | 0 | 11.1.2 | TV1207 feed wat. - req.pos. |  | TV1207 | P29 | FV | 1207 |  | _ | 10 | ZY | P29FV1207_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1020-10008 | 8 |  | P29TI1231 | feed wat. inlet drum - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1002 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 300 | °C |  | 11 |  | 11.1.4.2 | 2 | 16 | AI |  |  | 0 | 11.1.4 | wat. inlet drum - temp. |  | wat. | P29 | TI | 1231 |  |  |  |  | P29TI1231 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1020-10009 | 9 |  | P29FI1211 | attemp. feed wat. - flow |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1002 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 3 | t/h |  | 11 |  | 11.1.4.2 | 3 | 16 | AI |  |  | 0 | 11.1.4 | feed wat. - flow |  | feed | P29 | FI | 1211 |  |  |  |  | P29FI1211 | ok |  |  |  | 0 | 3 | t/h
ID-S01AP1020-10010 | 10 |  | P29LSLL1001 | drum - lev. LL |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1001 |  | S01AP1020 |  |  |  |  | DIS | SPST | false | = | active | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | - lev. LL |  | - | P29 | LSLL | 1001 |  |  |  |  | P29LSLL1001 | ok | [5 empty] | 0
ID-S01AP1020-10011 | 11 |  | P29LSHH1002 | drum - lev. HH |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1001 |  | S01AP1020 |  |  |  |  | DIS | SPST | false | = | active | 0 |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | - lev. HH |  | - | P29 | LSHH | 1002 |  |  |  |  | P29LSHH1002 | ok | [5 empty] | 0
ID-S01AP1020-10012 | 12 |  | P29LI1000Z | drum - lev. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1004 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 600 | mm |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | - lev. |  | - | P29 | LI | 1000 | Z |  |  |  | P29LI1000Z | ok |  |  |  | 0 | 600 | mm
ID-S01AP1020-10013 | 13 |  | P29LI1000X | drum - lev. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1003 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 600 | mm |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | - lev. |  | - | P29 | LI | 1000 | X |  |  |  | P29LI1000X | ok |  |  |  | 0 | 600 | mm
ID-S01AP1020-10014 | 14 |  | P29LI1000Y | drum - lev. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1003 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 600 | mm |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | - lev. |  | - | P29 | LI | 1000 | Y |  |  |  | P29LI1000Y | ok |  |  |  | 0 | 600 | mm
ID-S01AP1020-10015 | 15 |  | P29PI1007X | drum - press. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1003 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 50 | bar |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | - press. |  | - | P29 | PI | 1007 | X |  |  |  | P29PI1007X | ok |  |  |  | 0 | 50 | bar
ID-S01AP1020-10016 | 16 |  | P29PI1007Y | drum - press. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1003 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 50 | bar |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | - press. |  | - | P29 | PI | 1007 | Y |  |  |  | P29PI1007Y | ok |  |  |  | 0 | 50 | bar
ID-S01AP1020-10017 | 17 |  | P29TI1010 | sat. steam - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1002 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 11 |  | 11.1.4.2 | 4 | 16 | AI |  |  | 0 | 11.1.4 | steam - temp. |  | steam | P29 | TI | 1010 |  |  |  |  | P29TI1010 | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10018 | 18 |  | P29MOV1040_YLRE | vlv. MOV1040 purge drum - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 1 | 23 | DI |  |  | 0 | 11.1.2 | MOV1040 purge drum - in remote |  | MOV1040 | P29 | MOV | 1040 |  | _ | 11 | YLRE | P29MOV1040_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10019 | 19 |  | P29MOV1040_ZSH | vlv. MOV1040 purge drum - opened |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 2 | 23 | DI |  |  | 0 | 11.1.2 | MOV1040 purge drum - opened |  | MOV1040 | P29 | MOV | 1040 |  | _ | 11 | ZSH | P29MOV1040_ZSH | ok | [5 empty] | 0
ID-S01AP1020-10020 | 20 |  | P29MOV1040_ZSL | vlv. MOV1040 purge drum - closed |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 3 | 23 | DI |  |  | 0 | 11.1.2 | MOV1040 purge drum - closed |  | MOV1040 | P29 | MOV | 1040 |  | _ | 11 | ZSL | P29MOV1040_ZSL | ok | [5 empty] | 0
ID-S01AP1020-10021 | 21 |  | P29MOV1040_YS | vlv. MOV1040 purge drum - gen.fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.6 | 4 | 23 | DI |  |  | 0 | 11.1.2 | MOV1040 purge drum - gen.fault |  | MOV1040 | P29 | MOV | 1040 |  | _ | 11 | YS | P29MOV1040_YS | ok | [5 empty] | 0
ID-S01AP1020-10022 | 22 |  | P29MOV1040_HSH | vlv. MOV1040 purge drum - open |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 27 | 32 | DO |  |  | 0 | 11.1.3 | MOV1040 purge drum - open |  | MOV1040 | P29 | MOV | 1040 |  | _ | 11 | HSH | P29MOV1040_HSH | ok | [5 empty] | 0
ID-S01AP1020-10023 | 23 |  | P29MOV1040_HSL | vlv. MOV1040 purge drum - close |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 28 | 32 | DO |  |  | 0 | 11.1.3 | MOV1040 purge drum - close |  | MOV1040 | P29 | MOV | 1040 |  | _ | 11 | HSL | P29MOV1040_HSL | ok | [5 empty] | 0
ID-S01AP1020-10024 | 24 |  | P29MOV1040_HSLL | vlv. MOV1040 purge drum - pos. stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 29 | 32 | DO |  |  | 0 | 11.1.3 | MOV1040 purge drum - pos. stop |  | MOV1040 | P29 | MOV | 1040 |  | _ | 11 | HSLL | P29MOV1040_HSLL | ok | [5 empty] | 0
ID-S01AP1020-10025 | 25 |  | P29MOV1040_ZI | vlv. MOV1040 purge drum - position |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.4.4 | 12 | 14 | AI |  |  | 0 | 11.1.4 | MOV1040 purge drum - position |  | MOV1040 | P29 | MOV | 1040 |  | _ | 11 | ZI | P29MOV1040_ZI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-10026 | 26 |  | P29TI1111 | steam outlet SH LT - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1005 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 11 |  | 11.1.4.2 | 5 | 16 | AI |  |  | 0 | 11.1.4 | outlet SH LT - temp. |  | outlet | P29 | TI | 1111 |  |  |  |  | P29TI1111 | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10027 | 27 |  | P29ZI1110 | desuperh. DH1110 steam outlet SH LT - position |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1005 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.4.2 | 6 | 16 | AI |  |  | 0 | 11.1.4 | DH1110 steam outlet SH LT - position |  | DH1110 | P29 | ZI | 1110 |  |  |  |  | P29ZI1110 | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-10028 | 28 |  | P29ZY1110 | desuperh. DH1110 steam outlet SH LT - req.pos. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1005 |  | S01AP1020 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.2.1 | 4 | 6 | AO |  |  | 0 | 11.1.2 | DH1110 steam outlet SH LT - req.pos. |  | DH1110 | P29 | ZY | 1110 |  |  |  |  | P29ZY1110 | ok |  |  |  | 0 |  | %
ID-S01AP1020-10029 | 29 |  | P29TI1110 | steam inlet SH HT - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1005 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 11 |  | 11.1.4.2 | 7 | 16 | AI |  |  | 0 | 11.1.4 | inlet SH HT - temp. |  | inlet | P29 | TI | 1110 |  |  |  |  | P29TI1110 | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10030 | 30 |  | P29PI1126 | steam outlet SH HT - press. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1010 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 50 | bar |  | 11 |  | 11.1.3.7 | 4 | 15 | AI |  |  | 0 | 11.1.3 | outlet SH HT - press. |  | outlet | P29 | PI | 1126 |  |  |  |  | P29PI1126 | ok |  |  |  | 0 | 50 | bar
ID-S01AP1020-10031 | 31 |  | P29TI1106 | steam outlet SH HT - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1010 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 11 |  | 11.1.3.7 | 5 | 15 | AI |  |  | 0 | 11.1.3 | outlet SH HT - temp. |  | outlet | P29 | TI | 1106 |  |  |  |  | P29TI1106 | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10032 | 32 |  | P29TI1128X | steam outlet SH HT - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1011 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | outlet SH HT - temp. |  | outlet | P29 | TI | 1128 | X |  |  |  | P29TI1128X | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10033 | 33 |  | P29TI1128Y | steam outlet SH HT - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1011 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | outlet SH HT - temp. |  | outlet | P29 | TI | 1128 | Y |  |  |  | P29TI1128Y | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10034 | 34 |  | P29TI1128Z | steam outlet SH HT - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1011 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | outlet SH HT - temp. |  | outlet | P29 | TI | 1128 | Z |  |  |  | P29TI1128Z | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10035 | 35 |  | P29FI1128 | steam outlet SH HT - flow |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1010 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 20 | t/h |  | 11 |  | 11.1.3.7 | 6 | 15 | AI |  |  | 0 | 11.1.3 | outlet SH HT - flow |  | outlet | P29 | FI | 1128 |  |  |  |  | P29FI1128 | ok |  |  |  | 0 | 20 | t/h
ID-S01AP1020-10036 | 36 |  | P29PV1126_ZI | vlv. PV1126 vent steam SH HT - position |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1002 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.4.2 | 8 | 16 | AI |  |  | 0 | 11.1.4 | PV1126 vent steam SH HT - position |  | PV1126 | P29 | PV | 1126 |  | _ | 10 | ZI | P29PV1126_ZI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-10037 | 37 |  | P29PV1126_ZY | vlv. PV1126 vent steam SH HT - req.pos. |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | P29JB1002 |  | S01AP1020 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.2.1 | 5 | 6 | AO |  |  | 0 | 11.1.2 | PV1126 vent steam SH HT - req.pos. |  | PV1126 | P29 | PV | 1126 |  | _ | 10 | ZY | P29PV1126_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1020-10038 | 38 |  | P29MOV1137_YLRE | vlv. MOV1137 block steam SH HT - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 5 | 23 | DI |  |  | 0 | 11.1.2 | MOV1137 block steam SH HT - in remote |  | MOV1137 | P29 | MOV | 1137 |  | _ | 11 | YLRE | P29MOV1137_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10039 | 39 |  | P29MOV1137_ZSH | vlv. MOV1137 block steam SH HT - opened |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 6 | 23 | DI |  |  | 0 | 11.1.2 | MOV1137 block steam SH HT - opened |  | MOV1137 | P29 | MOV | 1137 |  | _ | 11 | ZSH | P29MOV1137_ZSH | ok | [5 empty] | 0
ID-S01AP1020-10040 | 40 |  | P29MOV1137_ZSL | vlv. MOV1137 block steam SH HT - closed |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 7 | 23 | DI |  |  | 0 | 11.1.2 | MOV1137 block steam SH HT - closed |  | MOV1137 | P29 | MOV | 1137 |  | _ | 11 | ZSL | P29MOV1137_ZSL | ok | [5 empty] | 0
ID-S01AP1020-10041 | 41 |  | P29MOV1137_YS | vlv. MOV1137 block steam SH HT - gen.fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.6 | 8 | 23 | DI |  |  | 0 | 11.1.2 | MOV1137 block steam SH HT - gen.fault |  | MOV1137 | P29 | MOV | 1137 |  | _ | 11 | YS | P29MOV1137_YS | ok | [5 empty] | 0
ID-S01AP1020-10042 | 42 |  | P29MOV1137_HSH | vlv. MOV1137 block steam SH HT - open |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 30 | 32 | DO |  |  | 0 | 11.1.3 | MOV1137 block steam SH HT - open |  | MOV1137 | P29 | MOV | 1137 |  | _ | 11 | HSH | P29MOV1137_HSH | ok | [5 empty] | 0
ID-S01AP1020-10043 | 43 |  | P29MOV1137_HSL | vlv. MOV1137 block steam SH HT - close |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 31 | 32 | DO |  |  | 0 | 11.1.3 | MOV1137 block steam SH HT - close |  | MOV1137 | P29 | MOV | 1137 |  | _ | 11 | HSL | P29MOV1137_HSL | ok | [5 empty] | 0
ID-S01AP1020-10044 | 44 |  | P29MOV1137_HSLL | vlv. MOV1137 block steam SH HT - pos. stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.3.4 | 32 | 32 | DO |  |  | 0 | 11.1.3 | MOV1137 block steam SH HT - pos. stop |  | MOV1137 | P29 | MOV | 1137 |  | _ | 11 | HSLL | P29MOV1137_HSLL | ok | [5 empty] | 0
ID-S01AP1020-10045 | 45 |  | P29MOV1137_ZI | vlv. MOV1137 block steam SH HT - position |  |  | ROT.KILN ST.GEN. 1 | P29 DP20 F | TBD |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.4.4 | 13 | 14 | AI |  |  | 0 | 11.1.4 | MOV1137 block steam SH HT - position |  | MOV1137 | P29 | MOV | 1137 |  | _ | 11 | ZI | P29MOV1137_ZI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-10046 | 46 |  | P29CY1310_YLRE | conveyor CY1310 extract. fly.ashes radiant - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 9 | 23 | DI |  |  | 0 | 11.1.2 | CY1310 extract. fly.ashes radiant - in remote |  | CY1310 | P29 | CY | 1310 |  | _ | 10 | YLRE | P29CY1310_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10047 | 47 |  | P29CY1310_YLH | conveyor CY1310 extract. fly.ashes radiant - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 10 | 23 | DI |  |  | 0 | 11.1.2 | CY1310 extract. fly.ashes radiant - in running |  | CY1310 | P29 | CY | 1310 |  | _ | 10 | YLH | P29CY1310_YLH | ok | [5 empty] | 0
ID-S01AP1020-10048 | 48 |  | P29CY1310_YSG | conveyor CY1310 extract. fly.ashes radiant - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 | 24 Vdc | 11 |  | 11.1.2.6 | 11 | 23 | DI |  |  | 0 | 11.1.2 | CY1310 extract. fly.ashes radiant - supply fault |  | CY1310 | P29 | CY | 1310 |  | _ | 10 | YSG | P29CY1310_YSG | ok | [5 empty] | 0
ID-S01AP1020-10049 | 49 |  | P29CY1310_HSH | conveyor CY1310 extract. fly.ashes radiant - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 9 | 30 | DO |  |  | 0 | 11.1.2 | CY1310 extract. fly.ashes radiant - start/stop |  | CY1310 | P29 | CY | 1310 |  | _ | 10 | HSH | P29CY1310_HSH | ok | [5 empty] | 0
ID-S01AP1020-10050 | 50 |  | P29FN1311_YLRE | fan FN1311 cool. fly.ashes conveyor - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 | 24 Vdc | 11 |  | 11.1.2.6 | 12 | 23 | DI |  |  | 0 | 11.1.2 | FN1311 cool. fly.ashes conveyor - in remote |  | FN1311 | P29 | FN | 1311 |  | _ | 10 | YLRE | P29FN1311_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10051 | 51 |  | P29FN1311_YLH | fan FN1311 cool. fly.ashes conveyor - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 13 | 23 | DI |  |  | 0 | 11.1.2 | FN1311 cool. fly.ashes conveyor - in running |  | FN1311 | P29 | FN | 1311 |  | _ | 10 | YLH | P29FN1311_YLH | ok | [5 empty] | 0
ID-S01AP1020-10052 | 52 |  | P29FN1311_YSG | fan FN1311 cool. fly.ashes conveyor - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 | 24 Vdc | 11 |  | 11.1.2.6 | 14 | 23 | DI |  |  | 0 | 11.1.2 | FN1311 cool. fly.ashes conveyor - supply fault |  | FN1311 | P29 | FN | 1311 |  | _ | 10 | YSG | P29FN1311_YSG | ok | [5 empty] | 0
ID-S01AP1020-10053 | 53 |  | P29FN1311_HSH | fan FN1311 cool. fly.ashes conveyor - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 10 | 30 | DO |  |  | 0 | 11.1.2 | FN1311 cool. fly.ashes conveyor - start/stop |  | FN1311 | P29 | FN | 1311 |  | _ | 10 | HSH | P29FN1311_HSH | ok | [5 empty] | 0
ID-S01AP1020-10054 | 54 |  | P29CY1312_YLRE | conveyor CY1312 extract. fly.ashes radiant - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 15 | 23 | DI |  |  | 0 | 11.1.2 | CY1312 extract. fly.ashes radiant - in remote |  | CY1312 | P29 | CY | 1312 |  | _ | 10 | YLRE | P29CY1312_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10055 | 55 |  | P29CY1312_YLH | conveyor CY1312 extract. fly.ashes radiant - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 16 | 23 | DI |  |  | 0 | 11.1.2 | CY1312 extract. fly.ashes radiant - in running |  | CY1312 | P29 | CY | 1312 |  | _ | 10 | YLH | P29CY1312_YLH | ok | [5 empty] | 0
ID-S01AP1020-10056 | 56 |  | P29CY1312_YSG | conveyor CY1312 extract. fly.ashes radiant - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 | 230 Vac | 11 |  | 11.1.2.6 | 17 | 23 | DI |  |  | 0 | 11.1.2 | CY1312 extract. fly.ashes radiant - supply fault |  | CY1312 | P29 | CY | 1312 |  | _ | 10 | YSG | P29CY1312_YSG | ok | [5 empty] | 0
ID-S01AP1020-10057 | 57 |  | P29CY1312_HSH | conveyor CY1312 extract. fly.ashes radiant - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 11 | 30 | DO |  |  | 0 | 11.1.2 | CY1312 extract. fly.ashes radiant - start/stop |  | CY1312 | P29 | CY | 1312 |  | _ | 10 | HSH | P29CY1312_HSH | ok | [5 empty] | 0
ID-S01AP1020-10058 | 58 |  | P29CY1313_YLRE | conveyor CY1313 extract. fly.ashes bypass - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 18 | 23 | DI |  |  | 0 | 11.1.2 | CY1313 extract. fly.ashes bypass - in remote |  | CY1313 | P29 | CY | 1313 |  | _ | 10 | YLRE | P29CY1313_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10059 | 59 |  | P29CY1313_YLH | conveyor CY1313 extract. fly.ashes bypass - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 19 | 23 | DI |  |  | 0 | 11.1.2 | CY1313 extract. fly.ashes bypass - in running |  | CY1313 | P29 | CY | 1313 |  | _ | 10 | YLH | P29CY1313_YLH | ok | [5 empty] | 0
ID-S01AP1020-10060 | 60 |  | P29CY1313_YSG | conveyor CY1313 extract. fly.ashes bypass - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.6 | 20 | 23 | DI |  |  | 0 | 11.1.2 | CY1313 extract. fly.ashes bypass - supply fault |  | CY1313 | P29 | CY | 1313 |  | _ | 10 | YSG | P29CY1313_YSG | ok | [5 empty] | 0
ID-S01AP1020-10061 | 61 |  | P29CY1313_HSH | conveyor CY1313 extract. fly.ashes bypass - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 12 | 30 | DO |  |  | 0 | 11.1.2 | CY1313 extract. fly.ashes bypass - start/stop |  | CY1313 | P29 | CY | 1313 |  | _ | 10 | HSH | P29CY1313_HSH | ok | [5 empty] | 0
ID-S01AP1020-10062 | 62 |  | P29CY1340_YLRE | conveyor CY1340 extract. fly.ashes convective - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 21 | 23 | DI |  |  | 0 | 11.1.2 | CY1340 extract. fly.ashes convective - in remote |  | CY1340 | P29 | CY | 1340 |  | _ | 10 | YLRE | P29CY1340_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10063 | 63 |  | P29CY1340_YLH | conveyor CY1340 extract. fly.ashes convective - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.2.6 | 22 | 23 | DI |  |  | 0 | 11.1.2 | CY1340 extract. fly.ashes convective - in running |  | CY1340 | P29 | CY | 1340 |  | _ | 10 | YLH | P29CY1340_YLH | ok | [5 empty] | 0
ID-S01AP1020-10064 | 64 |  | P29CY1340_YSG | conveyor CY1340 extract. fly.ashes convective - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.2.6 | 23 | 23 | DI |  |  | 0 | 11.1.2 | CY1340 extract. fly.ashes convective - supply fault |  | CY1340 | P29 | CY | 1340 |  | _ | 10 | YSG | P29CY1340_YSG | ok | [5 empty] | 0
ID-S01AP1020-10065 | 65 |  | P29CY1340_HSH | conveyor CY1340 extract. fly.ashes convective - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 13 | 30 | DO |  |  | 0 | 11.1.2 | CY1340 extract. fly.ashes convective - start/stop |  | CY1340 | P29 | CY | 1340 |  | _ | 10 | HSH | P29CY1340_HSH | ok | [5 empty] | 0
ID-S01AP1020-10066 | 66 |  | P29CLV1320_YLRE | clapet vlv. CLV1320 extract. fly.ashes radiant - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 1 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1320 extract. fly.ashes radiant - in remote |  | vlv. | P29 | CLV | 1320 |  | _ | 11 | YLRE | P29CLV1320_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10067 | 67 |  | P29CLV1320_YLH | clapet vlv. CLV1320 extract. fly.ashes radiant - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 2 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1320 extract. fly.ashes radiant - in running |  | vlv. | P29 | CLV | 1320 |  | _ | 11 | YLH | P29CLV1320_YLH | ok | [5 empty] | 0
ID-S01AP1020-10068 | 68 |  | P29CLV1320_YSG | clapet vlv. CLV1320 extract. fly.ashes radiant - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.1 | 3 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1320 extract. fly.ashes radiant - supply fault |  | vlv. | P29 | CLV | 1320 |  | _ | 11 | YSG | P29CLV1320_YSG | ok | [5 empty] | 0
ID-S01AP1020-10069 | 69 |  | P29CLV1320_HSH | clapet vlv. CLV1320 extract. fly.ashes radiant - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 14 | 30 | DO |  |  | 0 | 11.1.2 | vlv. CLV1320 extract. fly.ashes radiant - start/stop |  | vlv. | P29 | CLV | 1320 |  | _ | 11 | HSH | P29CLV1320_HSH | ok | [5 empty] | 0
ID-S01AP1020-10070 | 70 |  | P29CLV1321_YLRE | clapet vlv. CLV1321 extract. fly.ashes radiant - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 4 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1321 extract. fly.ashes radiant - in remote |  | vlv. | P29 | CLV | 1321 |  | _ | 11 | YLRE | P29CLV1321_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10071 | 71 |  | P29CLV1321_YLH | clapet vlv. CLV1321 extract. fly.ashes radiant - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 5 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1321 extract. fly.ashes radiant - in running |  | vlv. | P29 | CLV | 1321 |  | _ | 11 | YLH | P29CLV1321_YLH | ok | [5 empty] | 0
ID-S01AP1020-10072 | 72 |  | P29CLV1321_YSG | clapet vlv. CLV1321 extract. fly.ashes radiant - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.1 | 6 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1321 extract. fly.ashes radiant - supply fault |  | vlv. | P29 | CLV | 1321 |  | _ | 11 | YSG | P29CLV1321_YSG | ok | [5 empty] | 0
ID-S01AP1020-10073 | 73 |  | P29CLV1321_HSH | clapet vlv. CLV1321 extract. fly.ashes radiant - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 15 | 30 | DO |  |  | 0 | 11.1.2 | vlv. CLV1321 extract. fly.ashes radiant - start/stop |  | vlv. | P29 | CLV | 1321 |  | _ | 11 | HSH | P29CLV1321_HSH | ok | [5 empty] | 0
ID-S01AP1020-10074 | 74 |  | P29CLV1322_YLRE | clapet vlv. CLV1322 extract. fly.ashes SH HT/LT - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 7 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1322 extract. fly.ashes SH HT/LT - in remote |  | vlv. | P29 | CLV | 1322 |  | _ | 11 | YLRE | P29CLV1322_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10075 | 75 |  | P29CLV1322_YLH | clapet vlv. CLV1322 extract. fly.ashes SH HT/LT - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 8 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1322 extract. fly.ashes SH HT/LT - in running |  | vlv. | P29 | CLV | 1322 |  | _ | 11 | YLH | P29CLV1322_YLH | ok | [5 empty] | 0
ID-S01AP1020-10076 | 76 |  | P29CLV1322_YSG | clapet vlv. CLV1322 extract. fly.ashes SH HT/LT - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.1 | 9 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1322 extract. fly.ashes SH HT/LT - supply fault |  | vlv. | P29 | CLV | 1322 |  | _ | 11 | YSG | P29CLV1322_YSG | ok | [5 empty] | 0
ID-S01AP1020-10077 | 77 |  | P29CLV1322_HSH | clapet vlv. CLV1322 extract. fly.ashes SH HT/LT - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 16 | 30 | DO |  |  | 0 | 11.1.2 | vlv. CLV1322 extract. fly.ashes SH HT/LT - start/stop |  | vlv. | P29 | CLV | 1322 |  | _ | 11 | HSH | P29CLV1322_HSH | ok | [5 empty] | 0
ID-S01AP1020-10078 | 78 |  | P29CLV1323_YLRE | clapet vlv. CLV1323 extract. fly.ashes bypass - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 10 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1323 extract. fly.ashes bypass - in remote |  | vlv. | P29 | CLV | 1323 |  | _ | 11 | YLRE | P29CLV1323_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10079 | 79 |  | P29CLV1323_YLH | clapet vlv. CLV1323 extract. fly.ashes bypass - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 11 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1323 extract. fly.ashes bypass - in running |  | vlv. | P29 | CLV | 1323 |  | _ | 11 | YLH | P29CLV1323_YLH | ok | [5 empty] | 0
ID-S01AP1020-10080 | 80 |  | P29CLV1323_YSG | clapet vlv. CLV1323 extract. fly.ashes bypass - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.1 | 12 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1323 extract. fly.ashes bypass - supply fault |  | vlv. | P29 | CLV | 1323 |  | _ | 11 | YSG | P29CLV1323_YSG | ok | [5 empty] | 0
ID-S01AP1020-10081 | 81 |  | P29CLV1323_HSH | clapet vlv. CLV1323 extract. fly.ashes bypass - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 17 | 30 | DO |  |  | 0 | 11.1.2 | vlv. CLV1323 extract. fly.ashes bypass - start/stop |  | vlv. | P29 | CLV | 1323 |  | _ | 11 | HSH | P29CLV1323_HSH | ok | [5 empty] | 0
ID-S01AP1020-10082 | 82 |  | P29CLV1324_YLRE | clapet vlv. CLV1324 extract. fly.ashes EVA 1 - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 13 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1324 extract. fly.ashes EVA 1 - in remote |  | vlv. | P29 | CLV | 1324 |  | _ | 11 | YLRE | P29CLV1324_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10083 | 83 |  | P29CLV1324_YLH | clapet vlv. CLV1324 extract. fly.ashes EVA 1 - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 14 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1324 extract. fly.ashes EVA 1 - in running |  | vlv. | P29 | CLV | 1324 |  | _ | 11 | YLH | P29CLV1324_YLH | ok | [5 empty] | 0
ID-S01AP1020-10084 | 84 |  | P29CLV1324_YSG | clapet vlv. CLV1324 extract. fly.ashes EVA 1 - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.1 | 15 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1324 extract. fly.ashes EVA 1 - supply fault |  | vlv. | P29 | CLV | 1324 |  | _ | 11 | YSG | P29CLV1324_YSG | ok | [5 empty] | 0
ID-S01AP1020-10085 | 85 |  | P29CLV1324_HSH | clapet vlv. CLV1324 extract. fly.ashes EVA 1 - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 18 | 30 | DO |  |  | 0 | 11.1.2 | vlv. CLV1324 extract. fly.ashes EVA 1 - start/stop |  | vlv. | P29 | CLV | 1324 |  | _ | 11 | HSH | P29CLV1324_HSH | ok | [5 empty] | 0
ID-S01AP1020-10086 | 86 |  | P29CLV1325_YLRE | clapet vlv. CLV1325 extract. fly.ashes EVA 2 - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 16 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1325 extract. fly.ashes EVA 2 - in remote |  | vlv. | P29 | CLV | 1325 |  | _ | 11 | YLRE | P29CLV1325_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10087 | 87 |  | P29CLV1325_YLH | clapet vlv. CLV1325 extract. fly.ashes EVA 2 - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 17 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1325 extract. fly.ashes EVA 2 - in running |  | vlv. | P29 | CLV | 1325 |  | _ | 11 | YLH | P29CLV1325_YLH | ok | [5 empty] | 0
ID-S01AP1020-10088 | 88 |  | P29CLV1325_YSG | clapet vlv. CLV1325 extract. fly.ashes EVA 2 - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.1 | 18 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1325 extract. fly.ashes EVA 2 - supply fault |  | vlv. | P29 | CLV | 1325 |  | _ | 11 | YSG | P29CLV1325_YSG | ok | [5 empty] | 0
ID-S01AP1020-10089 | 89 |  | P29CLV1325_HSH | clapet vlv. CLV1325 extract. fly.ashes EVA 2 - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 19 | 30 | DO |  |  | 0 | 11.1.2 | vlv. CLV1325 extract. fly.ashes EVA 2 - start/stop |  | vlv. | P29 | CLV | 1325 |  | _ | 11 | HSH | P29CLV1325_HSH | ok | [5 empty] | 0
ID-S01AP1020-10090 | 90 |  | P29CLV1326_YLRE | clapet vlv. CLV1326 extract. fly.ashes ECO - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 19 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1326 extract. fly.ashes ECO - in remote |  | vlv. | P29 | CLV | 1326 |  | _ | 11 | YLRE | P29CLV1326_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10091 | 91 |  | P29CLV1326_YLH | clapet vlv. CLV1326 extract. fly.ashes ECO - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.1 | 20 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1326 extract. fly.ashes ECO - in running |  | vlv. | P29 | CLV | 1326 |  | _ | 11 | YLH | P29CLV1326_YLH | ok | [5 empty] | 0
ID-S01AP1020-10092 | 92 |  | P29CLV1326_YSG | clapet vlv. CLV1326 extract. fly.ashes ECO - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.1 | 21 | 30 | DI |  |  | 0 | 11.1.3 | vlv. CLV1326 extract. fly.ashes ECO - supply fault |  | vlv. | P29 | CLV | 1326 |  | _ | 11 | YSG | P29CLV1326_YSG | ok | [5 empty] | 0
ID-S01AP1020-10093 | 93 |  | P29CLV1326_HSH | clapet vlv. CLV1326 extract. fly.ashes ECO - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 20 | 30 | DO |  |  | 0 | 11.1.2 | vlv. CLV1326 extract. fly.ashes ECO - start/stop |  | vlv. | P29 | CLV | 1326 |  | _ | 11 | HSH | P29CLV1326_HSH | ok | [5 empty] | 0
ID-S01AP1020-10094 | 94 |  | P29HAM1503_YLRE | hammer HAM1503 extract. fly.ashes SH HT - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 1 | 26 | DI |  |  | 0 | 11.1.3 | HAM1503 extract. fly.ashes SH HT - in remote |  | HAM1503 | P29 | HAM | 1503 |  | _ | 11 | YLRE | P29HAM1503_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10095 | 95 |  | P29HAM1503_YLH | hammer HAM1503 extract. fly.ashes SH HT - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 2 | 26 | DI |  |  | 0 | 11.1.3 | HAM1503 extract. fly.ashes SH HT - in running |  | HAM1503 | P29 | HAM | 1503 |  | _ | 11 | YLH | P29HAM1503_YLH | ok | [5 empty] | 0
ID-S01AP1020-10096 | 96 |  | P29HAM1503_YSG | hammer HAM1503 extract. fly.ashes SH HT - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.2 | 3 | 26 | DI |  |  | 0 | 11.1.3 | HAM1503 extract. fly.ashes SH HT - supply fault |  | HAM1503 | P29 | HAM | 1503 |  | _ | 11 | YSG | P29HAM1503_YSG | ok | [5 empty] | 0
ID-S01AP1020-10097 | 97 |  | P29HAM1503_HSH | hammer HAM1503 extract. fly.ashes SH HT - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 21 | 30 | DO |  |  | 0 | 11.1.2 | HAM1503 extract. fly.ashes SH HT - start/stop |  | HAM1503 | P29 | HAM | 1503 |  | _ | 11 | HSH | P29HAM1503_HSH | ok | [5 empty] | 0
ID-S01AP1020-10098 | 98 |  | P29HAM1504_YLRE | hammer HAM1504 extract. fly.ashes SH LT - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 4 | 26 | DI |  |  | 0 | 11.1.3 | HAM1504 extract. fly.ashes SH LT - in remote |  | HAM1504 | P29 | HAM | 1504 |  | _ | 11 | YLRE | P29HAM1504_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10099 | 99 |  | P29HAM1504_YLH | hammer HAM1504 extract. fly.ashes SH LT - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 5 | 26 | DI |  |  | 0 | 11.1.3 | HAM1504 extract. fly.ashes SH LT - in running |  | HAM1504 | P29 | HAM | 1504 |  | _ | 11 | YLH | P29HAM1504_YLH | ok | [5 empty] | 0
ID-S01AP1020-10100 | 100 |  | P29HAM1504_YSG | hammer HAM1504 extract. fly.ashes SH LT - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.2 | 6 | 26 | DI |  |  | 0 | 11.1.3 | HAM1504 extract. fly.ashes SH LT - supply fault |  | HAM1504 | P29 | HAM | 1504 |  | _ | 11 | YSG | P29HAM1504_YSG | ok | [5 empty] | 0
ID-S01AP1020-10101 | 101 |  | P29HAM1504_HSH | hammer HAM1504 extract. fly.ashes SH LT - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 22 | 30 | DO |  |  | 0 | 11.1.2 | HAM1504 extract. fly.ashes SH LT - start/stop |  | HAM1504 | P29 | HAM | 1504 |  | _ | 11 | HSH | P29HAM1504_HSH | ok | [5 empty] | 0
ID-S01AP1020-10102 | 102 |  | P29HAM1505_YLRE | hammer HAM1505 extract. fly.ashes EVA 1 - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 7 | 26 | DI |  |  | 0 | 11.1.3 | HAM1505 extract. fly.ashes EVA 1 - in remote |  | HAM1505 | P29 | HAM | 1505 |  | _ | 11 | YLRE | P29HAM1505_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10103 | 103 |  | P29HAM1505_YLH | hammer HAM1505 extract. fly.ashes EVA 1 - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 8 | 26 | DI |  |  | 0 | 11.1.3 | HAM1505 extract. fly.ashes EVA 1 - in running |  | HAM1505 | P29 | HAM | 1505 |  | _ | 11 | YLH | P29HAM1505_YLH | ok | [5 empty] | 0
ID-S01AP1020-10104 | 104 |  | P29HAM1505_YSG | hammer HAM1505 extract. fly.ashes EVA 1 - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.2 | 9 | 26 | DI |  |  | 0 | 11.1.3 | HAM1505 extract. fly.ashes EVA 1 - supply fault |  | HAM1505 | P29 | HAM | 1505 |  | _ | 11 | YSG | P29HAM1505_YSG | ok | [5 empty] | 0
ID-S01AP1020-10105 | 105 |  | P29HAM1505_HSH | hammer HAM1505 extract. fly.ashes EVA 1 - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 23 | 30 | DO |  |  | 0 | 11.1.2 | HAM1505 extract. fly.ashes EVA 1 - start/stop |  | HAM1505 | P29 | HAM | 1505 |  | _ | 11 | HSH | P29HAM1505_HSH | ok | [5 empty] | 0
ID-S01AP1020-10106 | 106 |  | P29HAM1506_YLRE | hammer HAM1506 extract. fly.ashes EVA 1 - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 10 | 26 | DI |  |  | 0 | 11.1.3 | HAM1506 extract. fly.ashes EVA 1 - in remote |  | HAM1506 | P29 | HAM | 1506 |  | _ | 11 | YLRE | P29HAM1506_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10107 | 107 |  | P29HAM1506_YLH | hammer HAM1506 extract. fly.ashes EVA 1 - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 11 | 26 | DI |  |  | 0 | 11.1.3 | HAM1506 extract. fly.ashes EVA 1 - in running |  | HAM1506 | P29 | HAM | 1506 |  | _ | 11 | YLH | P29HAM1506_YLH | ok | [5 empty] | 0
ID-S01AP1020-10108 | 108 |  | P29HAM1506_YSG | hammer HAM1506 extract. fly.ashes EVA 1 - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.2 | 12 | 26 | DI |  |  | 0 | 11.1.3 | HAM1506 extract. fly.ashes EVA 1 - supply fault |  | HAM1506 | P29 | HAM | 1506 |  | _ | 11 | YSG | P29HAM1506_YSG | ok | [5 empty] | 0
ID-S01AP1020-10109 | 109 |  | P29HAM1506_HSH | hammer HAM1506 extract. fly.ashes EVA 1 - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 24 | 30 | DO |  |  | 0 | 11.1.2 | HAM1506 extract. fly.ashes EVA 1 - start/stop |  | HAM1506 | P29 | HAM | 1506 |  | _ | 11 | HSH | P29HAM1506_HSH | ok | [5 empty] | 0
ID-S01AP1020-10110 | 110 |  | P29HAM1507_YLRE | hammer HAM1507 extract. fly.ashes EVA 2 - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 13 | 26 | DI |  |  | 0 | 11.1.3 | HAM1507 extract. fly.ashes EVA 2 - in remote |  | HAM1507 | P29 | HAM | 1507 |  | _ | 11 | YLRE | P29HAM1507_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10111 | 111 |  | P29HAM1507_YLH | hammer HAM1507 extract. fly.ashes EVA 2 - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 14 | 26 | DI |  |  | 0 | 11.1.3 | HAM1507 extract. fly.ashes EVA 2 - in running |  | HAM1507 | P29 | HAM | 1507 |  | _ | 11 | YLH | P29HAM1507_YLH | ok | [5 empty] | 0
ID-S01AP1020-10112 | 112 |  | P29HAM1507_YSG | hammer HAM1507 extract. fly.ashes EVA 2 - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.2 | 15 | 26 | DI |  |  | 0 | 11.1.3 | HAM1507 extract. fly.ashes EVA 2 - supply fault |  | HAM1507 | P29 | HAM | 1507 |  | _ | 11 | YSG | P29HAM1507_YSG | ok | [5 empty] | 0
ID-S01AP1020-10113 | 113 |  | P29HAM1507_HSH | hammer HAM1507 extract. fly.ashes EVA 2 - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 25 | 30 | DO |  |  | 0 | 11.1.2 | HAM1507 extract. fly.ashes EVA 2 - start/stop |  | HAM1507 | P29 | HAM | 1507 |  | _ | 11 | HSH | P29HAM1507_HSH | ok | [5 empty] | 0
ID-S01AP1020-10114 | 114 |  | P29HAM1508_YLRE | hammer HAM1508 extract. fly.ashes EVA 2 - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 16 | 26 | DI |  |  | 0 | 11.1.3 | HAM1508 extract. fly.ashes EVA 2 - in remote |  | HAM1508 | P29 | HAM | 1508 |  | _ | 11 | YLRE | P29HAM1508_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10115 | 115 |  | P29HAM1508_YLH | hammer HAM1508 extract. fly.ashes EVA 2 - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 17 | 26 | DI |  |  | 0 | 11.1.3 | HAM1508 extract. fly.ashes EVA 2 - in running |  | HAM1508 | P29 | HAM | 1508 |  | _ | 11 | YLH | P29HAM1508_YLH | ok | [5 empty] | 0
ID-S01AP1020-10116 | 116 |  | P29HAM1508_YSG | hammer HAM1508 extract. fly.ashes EVA 2 - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.2 | 18 | 26 | DI |  |  | 0 | 11.1.3 | HAM1508 extract. fly.ashes EVA 2 - supply fault |  | HAM1508 | P29 | HAM | 1508 |  | _ | 11 | YSG | P29HAM1508_YSG | ok | [5 empty] | 0
ID-S01AP1020-10117 | 117 |  | P29HAM1508_HSH | hammer HAM1508 extract. fly.ashes EVA 2 - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 26 | 30 | DO |  |  | 0 | 11.1.2 | HAM1508 extract. fly.ashes EVA 2 - start/stop |  | HAM1508 | P29 | HAM | 1508 |  | _ | 11 | HSH | P29HAM1508_HSH | ok | [5 empty] | 0
ID-S01AP1020-10118 | 118 |  | P29HAM1509_YLRE | hammer HAM1509 extract. fly.ashes ECO - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 19 | 26 | DI |  |  | 0 | 11.1.3 | HAM1509 extract. fly.ashes ECO - in remote |  | HAM1509 | P29 | HAM | 1509 |  | _ | 11 | YLRE | P29HAM1509_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10119 | 119 |  | P29HAM1509_YLH | hammer HAM1509 extract. fly.ashes ECO - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 20 | 26 | DI |  |  | 0 | 11.1.3 | HAM1509 extract. fly.ashes ECO - in running |  | HAM1509 | P29 | HAM | 1509 |  | _ | 11 | YLH | P29HAM1509_YLH | ok | [5 empty] | 0
ID-S01AP1020-10120 | 120 |  | P29HAM1509_YSG | hammer HAM1509 extract. fly.ashes ECO - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.2 | 21 | 26 | DI |  |  | 0 | 11.1.3 | HAM1509 extract. fly.ashes ECO - supply fault |  | HAM1509 | P29 | HAM | 1509 |  | _ | 11 | YSG | P29HAM1509_YSG | ok | [5 empty] | 0
ID-S01AP1020-10121 | 121 |  | P29HAM1509_HSH | hammer HAM1509 extract. fly.ashes ECO - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 27 | 30 | DO |  |  | 0 | 11.1.2 | HAM1509 extract. fly.ashes ECO - start/stop |  | HAM1509 | P29 | HAM | 1509 |  | _ | 11 | HSH | P29HAM1509_HSH | ok | [5 empty] | 0
ID-S01AP1020-10122 | 122 |  | P29HAM1510_YLRE | hammer HAM1510 extract. fly.ashes ECO - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 22 | 26 | DI |  |  | 0 | 11.1.3 | HAM1510 extract. fly.ashes ECO - in remote |  | HAM1510 | P29 | HAM | 1510 |  | _ | 11 | YLRE | P29HAM1510_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10123 | 123 |  | P29HAM1510_YLH | hammer HAM1510 extract. fly.ashes ECO - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.3.2 | 23 | 26 | DI |  |  | 0 | 11.1.3 | HAM1510 extract. fly.ashes ECO - in running |  | HAM1510 | P29 | HAM | 1510 |  | _ | 11 | YLH | P29HAM1510_YLH | ok | [5 empty] | 0
ID-S01AP1020-10124 | 124 |  | P29HAM1510_YSG | hammer HAM1510 extract. fly.ashes ECO - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.3.2 | 24 | 26 | DI |  |  | 0 | 11.1.3 | HAM1510 extract. fly.ashes ECO - supply fault |  | HAM1510 | P29 | HAM | 1510 |  | _ | 11 | YSG | P29HAM1510_YSG | ok | [5 empty] | 0
ID-S01AP1020-10125 | 125 |  | P29HAM1510_HSH | hammer HAM1510 extract. fly.ashes ECO - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 28 | 30 | DO |  |  | 0 | 11.1.2 | HAM1510 extract. fly.ashes ECO - start/stop |  | HAM1510 | P29 | HAM | 1510 |  | _ | 11 | HSH | P29HAM1510_HSH | ok | [5 empty] | 0
ID-S01AP1020-10126 | 126 |  | P29TI1406 | flue gas radiant h1 - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1005 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 1400 | °C |  | 11 |  | 11.1.4.2 | 9 | 16 | AI |  |  | 0 | 11.1.4 | gas radiant h1 - temp. |  | gas | P29 | TI | 1406 |  |  |  |  | P29TI1406 | ok |  |  |  | 0 | 1400 | °C
ID-S01AP1020-10127 | 127 |  | P29SOV1909_HSH | vlv. SOV1909 cleaning pyrom. TT1406 - open/close |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1004 |  | S01AP1020 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 11 |  | 11.1.4.5 | 1 | 15 | DO |  |  | 0 | 11.1.4 | SOV1909 cleaning pyrom. TT1406 - open/close |  | SOV1909 | P29 | SOV | 1909 |  | _ | 11 | HSH | P29SOV1909_HSH | ok | [5 empty] | 0
ID-S01AP1020-10128 | 128 |  | P29TI1407 | flue gas radiant h2 - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1005 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 1400 | °C |  | 11 |  | 11.1.4.2 | 10 | 16 | AI |  |  | 0 | 11.1.4 | gas radiant h2 - temp. |  | gas | P29 | TI | 1407 |  |  |  |  | P29TI1407 | ok |  |  |  | 0 | 1400 | °C
ID-S01AP1020-10129 | 129 |  | P29SOV1914_HSH | vlv. SOV1914 cleaning pyrom. TT1407 - open/close |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1004 |  | S01AP1020 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 11 |  | 11.1.4.5 | 2 | 15 | DO |  |  | 0 | 11.1.4 | SOV1914 cleaning pyrom. TT1407 - open/close |  | SOV1914 | P29 | SOV | 1914 |  | _ | 11 | HSH | P29SOV1914_HSH | ok | [5 empty] | 0
ID-S01AP1020-10130 | 130 |  | P29TI1408 | flue gas radiant h3 - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1005 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 1400 | °C |  | 11 |  | 11.1.4.2 | 11 | 16 | AI |  |  | 0 | 11.1.4 | gas radiant h3 - temp. |  | gas | P29 | TI | 1408 |  |  |  |  | P29TI1408 | ok |  |  |  | 0 | 1400 | °C
ID-S01AP1020-10131 | 131 |  | P29SOV1919_HSH | vlv. SOV1919 cleaning pyrom. TT1408 - open/close |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1004 |  | S01AP1020 |  |  |  |  | DO | RELAY - 24 Vac | true | → | active | 0 |  | 11 |  | 11.1.4.5 | 3 | 15 | DO |  |  | 0 | 11.1.4 | SOV1919 cleaning pyrom. TT1408 - open/close |  | SOV1919 | P29 | SOV | 1919 |  | _ | 11 | HSH | P29SOV1919_HSH | ok | [5 empty] | 0
ID-S01AP1020-10132 | 132 |  | P29PI1409X | flue gas radiant - press. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1003 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | -7 | ∕ | +7 | mbar |  | 11 |  | 11.1.4.2 | 12 | 16 | AI |  |  | 0 | 11.1.4 | gas radiant - press. |  | gas | P29 | PI | 1409 | X |  |  |  | P29PI1409X | ok |  |  |  | -7 | +7 | mbar
ID-S01AP1020-10133 | 133 |  | P29PI1409Y | flue gas radiant - press. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1003 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | -7 | ∕ | +7 | mbar |  | 11 |  | 11.1.4.2 | 13 | 16 | AI |  |  | 0 | 11.1.4 | gas radiant - press. |  | gas | P29 | PI | 1409 | Y |  |  |  | P29PI1409Y | ok |  |  |  | -7 | +7 | mbar
ID-S01AP1020-10134 | 134 | P29OIT1410 | P29OIT1410-1 | flue gas radiant - oxig. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1005 |  | S01AP1020 |  |  |  |  | DI | SPST | 0 | = | 1000 | °C |  | 11 |  | 11.1.3.2 | 25 | 26 | DI |  |  | 0 | 11.1.3 | gas radiant - oxig. |  | gas | P29 | OIT | 1410 | - | 1 |  |  | P29OIT1410-1 | ok | [5 empty] | °C
ID-S01AP1020-10135 | 135 | P29OIT1410 | P29OIT1410-2 | flue gas radiant - oxig. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1005 |  | S01AP1020 |  |  |  |  | DI | SPST | 0 | = | 1000 | °C |  | 11 |  | 11.1.3.2 | 26 | 26 | DI |  |  | 0 | 11.1.3 | gas radiant - oxig. |  | gas | P29 | OIT | 1410 | - | 2 |  |  | P29OIT1410-2 | ok | [5 empty] | °C
ID-S01AP1020-10136 | 136 |  | P29OI1410 | flue gas radiant - oxig. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1005 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 1000 | °C |  | 11 |  | 11.1.4.2 | 14 | 16 | AI |  |  | 0 | 11.1.4 | gas radiant - oxig. |  | gas | P29 | OI | 1410 |  |  |  |  | P29OI1410 | ok |  |  |  | 0 | 1000 | °C
ID-S01AP1020-10137 | 137 |  | P29PI1419 | flue gas inlet SH HT - press. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1006 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | -15 | ∕ | 5 | mbar |  | 11 |  | 11.1.3.7 | 7 | 15 | AI |  |  | 0 | 11.1.3 | gas inlet SH HT - press. |  | gas | P29 | PI | 1419 |  |  |  |  | P29PI1419 | ok |  |  |  | -15 | 5 | mbar
ID-S01AP1020-10138 | 138 |  | P29PI1440 | flue gas outlet boiler - press. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1006 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | -15 | ∕ | 5 | mbar |  | 11 |  | 11.1.3.7 | 8 | 15 | AI |  |  | 0 | 11.1.3 | gas outlet boiler - press. |  | gas | P29 | PI | 1440 |  |  |  |  | P29PI1440 | ok |  |  |  | -15 | 5 | mbar
ID-S01AP1020-10139 | 139 |  | P29TI1417 | flue gas inlet SH HT - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1006 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 800 | °C |  | 11 |  | 11.1.3.7 | 9 | 15 | AI |  |  | 0 | 11.1.3 | gas inlet SH HT - temp. |  | gas | P29 | TI | 1417 |  |  |  |  | P29TI1417 | ok |  |  |  | 0 | 800 | °C
ID-S01AP1020-10140 | 140 |  | P29TI1428 | flue gas inlet EVA 1 - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1006 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 11 |  | 11.1.3.7 | 10 | 15 | AI |  |  | 0 | 11.1.3 | gas inlet EVA 1 - temp. |  | gas | P29 | TI | 1428 |  |  |  |  | P29TI1428 | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10141 | 141 |  | P29TI1434 | flue gas inlet ECO - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1006 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 11 |  | 11.1.3.7 | 11 | 15 | AI |  |  | 0 | 11.1.3 | gas inlet ECO - temp. |  | gas | P29 | TI | 1434 |  |  |  |  | P29TI1434 | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10142 | 142 |  | P29TI1436X | flue gas outlet boiler - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1006 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 800 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | gas outlet boiler - temp. |  | gas | P29 | TI | 1436 | X |  |  |  | P29TI1436X | ok |  |  |  | 0 | 800 | °C
ID-S01AP1020-10143 | 143 |  | P29TI1436Y | flue gas outlet boiler - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1006 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 800 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | gas outlet boiler - temp. |  | gas | P29 | TI | 1436 | Y |  |  |  | P29TI1436Y | ok |  |  |  | 0 | 800 | °C
ID-S01AP1020-10144 | 144 |  | P29TI1435 | flue gas outlet ECO - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | TBD |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 400 | °C |  | 11 |  | 11.1.4.4 | 14 | 14 | AI |  |  | 0 | 11.1.4 | gas outlet ECO - temp. |  | gas | P29 | TI | 1435 |  |  |  |  | P29TI1435 | ok |  |  |  | 0 | 400 | °C
ID-S01AP1020-10145 | 145 |  | P29FV1436_ZI | vlv. FV1436 flue gas outlet boiler - position |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P29JB1007 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 4W | 0 | ∕ | 100 | % |  | 11 |  | 11.1.3.7 | 12 | 15 | AI |  |  | 0 | 11.1.3 | FV1436 flue gas outlet boiler - position |  | FV1436 | P29 | FV | 1436 |  | _ | 10 | ZI | P29FV1436_ZI | ok |  |  |  | 0 | 100 | %
ID-S01AP1020-10146 | 146 |  | P29FV1436_ZY | vlv. FV1436 flue gas outlet boiler - req.pos. |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P29JB1007 |  | S01AP1020 |  |  |  |  | AO | 4/20 mA | 0 | ∕ | 100 | % |  | 11 |  | 11.1.2.1 | 6 | 6 | AO |  |  | 0 | 11.1.2 | FV1436 flue gas outlet boiler - req.pos. |  | FV1436 | P29 | FV | 1436 |  | _ | 10 | ZY | P29FV1436_ZY | ok |  |  |  | 0 |  | %
ID-S01AP1020-10147 | 147 |  | P29CY1310_SE | conveyor CY1310 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 1 | 10 | DI |  |  | 0 | 11.1.3 | CY1310 - speed sens. |  | CY1310 | P29 | CY | 1310 |  | _ | 10 | SE | P29CY1310_SE | ok | [5 empty] | 0
ID-S01AP1020-10148 | 148 |  | P29CY1312_SE | conveyor CY1312 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 2 | 10 | DI |  |  | 0 | 11.1.3 | CY1312 - speed sens. |  | CY1312 | P29 | CY | 1312 |  | _ | 10 | SE | P29CY1312_SE | ok | [5 empty] | 0
ID-S01AP1020-10149 | 149 |  | P29CY1313_SE | conveyor CY1313 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 3 | 10 | DI |  |  | 0 | 11.1.3 | CY1313 - speed sens. |  | CY1313 | P29 | CY | 1313 |  | _ | 10 | SE | P29CY1313_SE | ok | [5 empty] | 0
ID-S01AP1020-10150 | 150 |  | P29CY1340_SE | conveyor CY1340 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 4 | 10 | DI |  |  | 0 | 11.1.3 | CY1340 - speed sens. |  | CY1340 | P29 | CY | 1340 |  | _ | 10 | SE | P29CY1340_SE | ok | [5 empty] | 0
ID-S01AP1020-10151 | 151 |  | P29RV1320X_SE | clapet vlv. RV1320 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 5 | 10 | DI |  |  | 0 | 11.1.3 | vlv. RV1320 - speed sens. |  | vlv. | P29 | RV | 1320 | X | _ | 11 | SE | P29RV1320X_SE | ok | [5 empty] | 0
ID-S01AP1020-10152 | 152 |  | P29RV1321X_SE | clapet vlv. RV1321 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 6 | 10 | DI |  |  | 0 | 11.1.3 | vlv. RV1321 - speed sens. |  | vlv. | P29 | RV | 1321 | X | _ | 11 | SE | P29RV1321X_SE | ok | [5 empty] | 0
ID-S01AP1020-10153 | 153 |  | P29RV1322X_SE | clapet vlv. RV1322 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 7 | 10 | DI |  |  | 0 | 11.1.3 | vlv. RV1322 - speed sens. |  | vlv. | P29 | RV | 1322 | X | _ | 11 | SE | P29RV1322X_SE | ok | [5 empty] | 0
ID-S01AP1020-10154 | 154 |  | P29RV1323X_SE | clapet vlv. RV1323 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 8 | 10 | DI |  |  | 0 | 11.1.3 | vlv. RV1323 - speed sens. |  | vlv. | P29 | RV | 1323 | X | _ | 11 | SE | P29RV1323X_SE | ok | [5 empty] | 0
ID-S01AP1020-10155 | 155 |  | P29RV1324X_SE | clapet vlv. RV1324 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1012 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 9 | 10 | DI |  |  | 0 | 11.1.3 | vlv. RV1324 - speed sens. |  | vlv. | P29 | RV | 1324 | X | _ | 11 | SE | P29RV1324X_SE | ok | [5 empty] | 0
ID-S01AP1020-10156 | 156 |  | P29RV1325X_SE | clapet vlv. RV1325 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1012 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.3.3 | 10 | 10 | DI |  |  | 0 | 11.1.3 | vlv. RV1325 - speed sens. |  | vlv. | P29 | RV | 1325 | X | _ | 11 | SE | P29RV1325X_SE | ok | [5 empty] | 0
ID-S01AP1020-10157 | 157 |  | P29RV1326X_SE | clapet vlv. RV1326 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1012 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.4.8 | 1 | 27 | DI |  |  | 0 | 11.1.4 | vlv. RV1326 - speed sens. |  | vlv. | P29 | RV | 1326 | X | _ | 11 | SE | P29RV1326X_SE | ok | [5 empty] | 0
ID-S01AP1020-10158 | 158 |  | P29RV1320Y_SE | clapet vlv. RV1320 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.4.8 | 2 | 27 | DI |  |  | 0 | 11.1.4 | vlv. RV1320 - speed sens. |  | vlv. | P29 | RV | 1320 | Y | _ | 11 | SE | P29RV1320Y_SE | ok | [5 empty] | 0
ID-S01AP1020-10159 | 159 |  | P29RV1321Y_SE | clapet vlv. RV1321 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.4.8 | 3 | 27 | DI |  |  | 0 | 11.1.4 | vlv. RV1321 - speed sens. |  | vlv. | P29 | RV | 1321 | Y | _ | 11 | SE | P29RV1321Y_SE | ok | [5 empty] | 0
ID-S01AP1020-10160 | 160 |  | P29RV1322Y_SE | clapet vlv. RV1322 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.4.8 | 4 | 27 | DI |  |  | 0 | 11.1.4 | vlv. RV1322 - speed sens. |  | vlv. | P29 | RV | 1322 | Y | _ | 11 | SE | P29RV1322Y_SE | ok | [5 empty] | 0
ID-S01AP1020-10161 | 161 |  | P29RV1323Y_SE | clapet vlv. RV1323 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.4.8 | 5 | 27 | DI |  |  | 0 | 11.1.4 | vlv. RV1323 - speed sens. |  | vlv. | P29 | RV | 1323 | Y | _ | 11 | SE | P29RV1323Y_SE | ok | [5 empty] | 0
ID-S01AP1020-10162 | 162 |  | P29RV1324Y_SE | clapet vlv. RV1324 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1008 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.4.8 | 6 | 27 | DI |  |  | 0 | 11.1.4 | vlv. RV1324 - speed sens. |  | vlv. | P29 | RV | 1324 | Y | _ | 11 | SE | P29RV1324Y_SE | ok | [5 empty] | 0
ID-S01AP1020-10163 | 163 |  | P29RV1325Y_SE | clapet vlv. RV1325 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1012 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.4.8 | 7 | 27 | DI |  |  | 0 | 11.1.4 | vlv. RV1325 - speed sens. |  | vlv. | P29 | RV | 1325 | Y | _ | 11 | SE | P29RV1325Y_SE | ok | [5 empty] | 0
ID-S01AP1020-10164 | 164 |  | P29RV1326Y_SE | clapet vlv. RV1326 - speed sens. |  |  | ROT.KILN ST.GEN. 1 | P29 DP30 F | P29JB1012 |  | S01AP1020 |  |  |  |  | DI | open collector | xxx | = | active | 0 |  | 11 |  | 11.1.4.8 | 8 | 27 | DI |  |  | 0 | 11.1.4 | vlv. RV1326 - speed sens. |  | vlv. | P29 | RV | 1326 | Y | _ | 11 | SE | P29RV1326Y_SE | ok | [5 empty] | 0
ID-S01AP1020-10165 | 165 |  | P29PM1601A_YLRE | pmp. PM1601A cool.wat. for flue gas vlv. - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.3.1 | 22 | 30 | DI |  |  | 0 | 11.1.3 | PM1601A cool.wat. for flue gas vlv. - in remote |  | PM1601A | P29 | PM | 1601 | A | _ | 11 | YLRE | P29PM1601A_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10166 | 166 |  | P29PM1601A_YLH | pmp. PM1601A cool.wat. for flue gas vlv. - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.3.1 | 23 | 30 | DI |  |  | 0 | 11.1.3 | PM1601A cool.wat. for flue gas vlv. - in running |  | PM1601A | P29 | PM | 1601 | A | _ | 11 | YLH | P29PM1601A_YLH | ok | [5 empty] | 0
ID-S01AP1020-10167 | 167 |  | P29PM1601A_YSG | pmp. PM1601A cool.wat. for flue gas vlv. - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 | A | 11.1.3.1 | 24 | 30 | DI |  |  | 0 | 11.1.3 | PM1601A cool.wat. for flue gas vlv. - supply fault |  | PM1601A | P29 | PM | 1601 | A | _ | 11 | YSG | P29PM1601A_YSG | ok | [5 empty] | 0
ID-S01AP1020-10168 | 168 |  | P29PM1601A_HSH | pmp. PM1601A cool.wat. for flue gas vlv. - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 29 | 30 | DO |  |  | 0 | 11.1.2 | PM1601A cool.wat. for flue gas vlv. - start/stop |  | PM1601A | P29 | PM | 1601 | A | _ | 11 | HSH | P29PM1601A_HSH | ok | [5 empty] | 0
ID-S01AP1020-10169 | 169 |  | P29PM1601B_YLRE | pmp. PM1601B cool.wat. for flue gas vlv. - in remote |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.4.8 | 9 | 27 | DI |  |  | 0 | 11.1.4 | PM1601B cool.wat. for flue gas vlv. - in remote |  | PM1601B | P29 | PM | 1601 | B | _ | 11 | YLRE | P29PM1601B_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10170 | 170 |  | P29PM1601B_YLH | pmp. PM1601B cool.wat. for flue gas vlv. - in running |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.4.8 | 10 | 27 | DI |  |  | 0 | 11.1.4 | PM1601B cool.wat. for flue gas vlv. - in running |  | PM1601B | P29 | PM | 1601 | B | _ | 11 | YLH | P29PM1601B_YLH | ok | [5 empty] | 0
ID-S01AP1020-10171 | 171 |  | P29PM1601B_YSG | pmp. PM1601B cool.wat. for flue gas vlv. - supply fault |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P23MCC1001 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 | B | 11.1.4.8 | 11 | 27 | DI |  |  | 0 | 11.1.4 | PM1601B cool.wat. for flue gas vlv. - supply fault |  | PM1601B | P29 | PM | 1601 | B | _ | 11 | YSG | P29PM1601B_YSG | ok | [5 empty] | 0
ID-S01AP1020-10172 | 172 |  | P29PM1601B_HSH | pmp. PM1601B cool.wat. for flue gas vlv. - start/stop |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P23MCC1001 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.2.5 | 30 | 30 | DO |  |  | 0 | 11.1.2 | PM1601B cool.wat. for flue gas vlv. - start/stop |  | PM1601B | P29 | PM | 1601 | B | _ | 11 | HSH | P29PM1601B_HSH | ok | [5 empty] | 0
ID-S01AP1020-10173 | 173 |  | P29FSLL1601 | cool.wat. - flow LL |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P29JB1012 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.4.8 | 12 | 27 | DI |  |  | 0 | 11.1.4 | - flow LL |  | - | P29 | FSLL | 1601 |  |  |  |  | P29FSLL1601 | ok | [5 empty] | 0
ID-S01AP1020-10174 | 174 |  | P29TI1602 | cool.wat. inlet FV 1436 - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P29JB1006 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 300 | °C |  | 11 |  | 11.1.3.7 | 13 | 15 | AI |  |  | 0 | 11.1.3 | inlet FV 1436 - temp. |  | inlet | P29 | TI | 1602 |  |  |  |  | P29TI1602 | ok |  |  |  | 0 | 300 | °C
ID-S01AP1020-10175 | 175 |  | P29PI1601 | cool.wat. outlet FV 1436 - press. |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P29JB1006 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 10 | bar |  | 11 |  | 11.1.3.7 | 14 | 15 | AI |  |  | 0 | 11.1.3 | outlet FV 1436 - press. |  | outlet | P29 | PI | 1601 |  |  |  |  | P29PI1601 | ok |  |  |  | 0 | 10 | bar
ID-S01AP1020-10176 | 176 |  | P29TI1601X | cool.wat. outlet FV 1436 - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P29JB1006 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 300 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | outlet FV 1436 - temp. |  | outlet | P29 | TI | 1601 | X |  |  |  | P29TI1601X | ok |  |  |  | 0 | 300 | °C
ID-S01AP1020-10177 | 177 |  | P29TI1601Y | cool.wat. outlet FV 1436 - temp. |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P29JB1006 |  | S01AP1020 |  |  |  |  | AIS | 4/20 mA - 2W | 0 | ∕ | 300 | °C |  | 31 |  |  | 0 | 0 | #N/A |  |  | 1 |  | outlet FV 1436 - temp. |  | outlet | P29 | TI | 1601 | Y |  |  |  | P29TI1601Y | ok |  |  |  | 0 | 300 | °C
ID-S01AP1020-10178 | 178 |  | P29FI1601 | cool.wat. - flow |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | P29JB1006 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 10 | t/h |  | 11 |  | 11.1.3.7 | 15 | 15 | AI |  |  | 0 | 11.1.3 | - flow |  | - | P29 | FI | 1601 |  |  |  |  | P29FI1601 | ok |  |  |  | 0 | 10 | t/h
ID-S01AP1020-10179 | 179 |  | P29POV1612_ZSH | vlv. POV1612 cool.wat. outlet pmp. - opened |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | HEPT |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.8 | 13 | 27 | DI |  |  | 0 | 11.1.4 | POV1612 cool.wat. outlet pmp. - opened |  | POV1612 | P29 | POV | 1612 |  | _ | 11 | ZSH | P29POV1612_ZSH | ok | [5 empty] | 0
ID-S01AP1020-10180 | 180 |  | P29POV1612_ZSL | vlv. POV1612 cool.wat. outlet pmp. - closed |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | HEPT |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.8 | 14 | 27 | DI |  |  | 0 | 11.1.4 | POV1612 cool.wat. outlet pmp. - closed |  | POV1612 | P29 | POV | 1612 |  | _ | 11 | ZSL | P29POV1612_ZSL | ok | [5 empty] | 0
ID-S01AP1020-10181 | 181 |  | P29POV1612_HSH | vlv. POV1612 cool.wat. outlet pmp. - open/close |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | HEPT |  | S01AP1020 |  |  |  |  | DO | RELAY - 24 Vac | true | → | open | 0 |  | 11 |  | 11.1.4.5 | 4 | 15 | DO |  |  | 0 | 11.1.4 | POV1612 cool.wat. outlet pmp. - open/close |  | POV1612 | P29 | POV | 1612 |  | _ | 11 | HSH | P29POV1612_HSH | ok | [5 empty] | 0
ID-S01AP1020-10182 | 182 |  | P29FV1613_ZSH | vlv. POV1613 cool.wat. outlet FV 1436 - opened |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | HEPT |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.8 | 15 | 27 | DI |  |  | 0 | 11.1.4 | POV1613 cool.wat. outlet FV 1436 - opened |  | POV1613 | P29 | FV | 1613 |  | _ | 10 | ZSH | P29FV1613_ZSH | ok | [5 empty] | 0
ID-S01AP1020-10183 | 183 |  | P29FV1613_ZSL | vlv. POV1613 cool.wat. outlet FV 1436 - closed |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | HEPT |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.8 | 16 | 27 | DI |  |  | 0 | 11.1.4 | POV1613 cool.wat. outlet FV 1436 - closed |  | POV1613 | P29 | FV | 1613 |  | _ | 10 | ZSL | P29FV1613_ZSL | ok | [5 empty] | 0
ID-S01AP1020-10184 | 184 |  | P29FV1613_HSH | vlv. POV1613 cool.wat. outlet FV 1436 - open/close |  |  | ROT.KILN ST.GEN. 1 | P29 DP60 E | HEPT |  | S01AP1020 |  |  |  |  | DO | RELAY - 24 Vac | true | → | open | 0 |  | 11 |  | 11.1.4.5 | 5 | 15 | DO |  |  | 0 | 11.1.4 | POV1613 cool.wat. outlet FV 1436 - open/close |  | POV1613 | P29 | FV | 1613 |  | _ | 10 | HSH | P29FV1613_HSH | ok | [5 empty] | 0
ID-S01AP1020-10185 | 185 |  | P34CAP1701_YLRE | cmd.aut.pan. CAP1701 ammon. SNCR - in remote |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.8 | 17 | 27 | DI |  |  | 0 | 11.1.4 | CAP1701 ammon. SNCR - in remote |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | YLRE | P34CAP1701_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10186 | 186 |  | P34CAP1701_YLH | cmd.aut.pan. CAP1701 ammon. SNCR - in running |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.8 | 18 | 27 | DI |  |  | 0 | 11.1.4 | CAP1701 ammon. SNCR - in running |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | YLH | P34CAP1701_YLH | ok | [5 empty] | 0
ID-S01AP1020-10187 | 187 |  | P34CAP1701_YSH | cmd.aut.pan. CAP1701 ammon. SNCR - com.trip |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 |  | 11.1.4.8 | 19 | 27 | DI |  |  | 0 | 11.1.4 | CAP1701 ammon. SNCR - com.trip |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | YSH | P34CAP1701_YSH | ok | [5 empty] | 0
ID-S01AP1020-10188 | 188 |  | P34CAP1701_HSH | cmd.aut.pan. CAP1701 ammon. SNCR - enable |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.4.5 | 6 | 15 | DO |  |  | 0 | 11.1.4 | CAP1701 ammon. SNCR - enable |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | HSH | P34CAP1701_HSH | ok | [5 empty] | 0
ID-S01AP1020-10189 | 189 |  | P34CAP1701_HSL | cmd.aut.pan. CAP1701 ammon. SNCR - disable |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.4.5 | 7 | 15 | DO |  |  | 0 | 11.1.4 | CAP1701 ammon. SNCR - disable |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | HSL | P34CAP1701_HSL | ok | [5 empty] | 0
ID-S01AP1020-10190 | 190 |  | P34CAP1701_HSR | cmd.aut.pan. CAP1701 ammon. SNCR - reset |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | active | 0 |  | 11 |  | 11.1.4.5 | 8 | 15 | DO |  |  | 0 | 11.1.4 | CAP1701 ammon. SNCR - reset |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | HSR | P34CAP1701_HSR | ok | [5 empty] | 0
ID-S01AP1020-10191 | 191 |  | P34CAP1701_HSK | cmd.aut.pan. CAP1701 ammon. SNCR - interlock |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | DO | RELAY | false | → | active | 0 |  | 11 |  | 11.1.4.5 | 9 | 15 | DO |  |  | 0 | 11.1.4 | CAP1701 ammon. SNCR - interlock |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | HSK | P34CAP1701_HSK | ok | [5 empty] | 0
ID-S01AP1020-10192 | 192 |  | P34CAP1701_TY | cmd.aut.pan. CAP1701 ammon. SNCR - PCZ flue gas - temp. |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | AO | 4/20 mA | xxx | ∕ | xxx | °C |  | 11 |  | 11.1.3.8 | 3 | 6 | AO |  |  | 0 | 11.1.3 | CAP1701 ammon. SNCR - PCZ flue gas - temp. |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | TY | P34CAP1701_TY | ok |  |  |  | xxx |  | °C
ID-S01AP1020-10193 | 193 |  | P34CAP1701_FY | cmd.aut.pan. CAP1701 ammon. SNCR - SH steam - flow in waste comb. |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | AO | 4/20 mA | xxx | ∕ | xxx | t/h |  | 11 |  | 11.1.3.8 | 4 | 6 | AO |  |  | 0 | 11.1.3 | CAP1701 ammon. SNCR - SH steam - flow in waste comb. |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | FY | P34CAP1701_FY | ok |  |  |  | xxx |  | t/h
ID-S01AP1020-10194 | 194 | P34CAP1701_AY | P34CAP1701_AY-1 | cmd.aut.pan. CAP1701 ammon. SNCR - NH3 outlet filter - conc. |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | AO | 4/20 mA | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.3.8 | 5 | 6 | AO |  |  | 0 | 11.1.3 | CAP1701 ammon. SNCR - NH3 outlet filter - conc. |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | AY-1 | P34CAP1701_AY-1 | ok |  |  |  | xxx |  | xxx
ID-S01AP1020-10195 | 195 | P34CAP1701_AY | P34CAP1701_AY-2 | cmd.aut.pan. CAP1701 ammon. SNCR - NOX outlet boiler - conc. |  |  | ROT.KILN ST.GEN. 1 | P34 DP50 D | P34CAP1701 |  | S01AP1020 |  |  |  |  | AO | 4/20 mA | xxx | ∕ | xxx | xxx |  | 11 |  | 11.1.3.8 | 6 | 6 | AO |  |  | 0 | 11.1.3 | CAP1701 ammon. SNCR - NOX outlet boiler - conc. |  | CAP1701 | P34 | CAP | 1701 |  | _ | 11 | AY-2 | P34CAP1701_AY-2 | ok |  |  |  | xxx |  | xxx
ID-S01AP1020-10196 | 196 |  | A23SR1640_YLRE | stir. SR1640 reag. deox. - in remote |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.8 | 20 | 27 | DI |  |  | 0 | 11.1.4 | SR1640 reag. deox. - in remote |  | SR1640 | A23 | SR | 1640 |  | _ | 10 | YLRE | A23SR1640_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10197 | 197 |  | A23SR1640_YLH | stir. SR1640 reag. deox. - in running |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.8 | 21 | 27 | DI |  |  | 0 | 11.1.4 | SR1640 reag. deox. - in running |  | SR1640 | A23 | SR | 1640 |  | _ | 10 | YLH | A23SR1640_YLH | ok | [5 empty] | 0
ID-S01AP1020-10198 | 198 |  | A23SR1640_HSH | stir. SR1640 reag. deox. - start/stop |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.4.5 | 10 | 15 | DO |  |  | 0 | 11.1.4 | SR1640 reag. deox. - start/stop |  | SR1640 | A23 | SR | 1640 |  | _ | 10 | HSH | A23SR1640_HSH | ok | [5 empty] | 0
ID-S01AP1020-10199 | 199 |  | A23LI1640 | reag. deox. - lev. |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 1000 | mm |  | 11 |  | 11.1.4.2 | 15 | 16 | AI |  |  | 0 | 11.1.4 | deox. - lev. |  | deox. | A23 | LI | 1640 |  |  |  |  | A23LI1640 | ok |  |  |  | 0 | 1000 | mm
ID-S01AP1020-10200 | 200 |  | A23PM1645A_YLRE | pmp. PM1645A dosage reag. deox. - in remote |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.3.1 | 25 | 30 | DI |  |  | 0 | 11.1.3 | PM1645A dosage reag. deox. - in remote |  | PM1645A | A23 | PM | 1645 | A | _ | 11 | YLRE | A23PM1645A_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10201 | 201 |  | A23PM1645A_YLH | pmp. PM1645A dosage reag. deox. - in running |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.3.1 | 26 | 30 | DI |  |  | 0 | 11.1.3 | PM1645A dosage reag. deox. - in running |  | PM1645A | A23 | PM | 1645 | A | _ | 11 | YLH | A23PM1645A_YLH | ok | [5 empty] | 0
ID-S01AP1020-10202 | 202 |  | A23PM1645A_YSG | pmp. PM1645A dosage reag. deox. - supply fault |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 | A | 11.1.3.1 | 27 | 30 | DI |  |  | 0 | 11.1.3 | PM1645A dosage reag. deox. - supply fault |  | PM1645A | A23 | PM | 1645 | A | _ | 11 | YSG | A23PM1645A_YSG | ok | [5 empty] | 0
ID-S01AP1020-10203 | 203 |  | A23PM1645A_HSH | pmp. PM1645A dosage reag. deox. - start/stop |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.4.5 | 11 | 15 | DO |  |  | 0 | 11.1.4 | PM1645A dosage reag. deox. - start/stop |  | PM1645A | A23 | PM | 1645 | A | _ | 11 | HSH | A23PM1645A_HSH | ok | [5 empty] | 0
ID-S01AP1020-10204 | 204 |  | A23PM1645B_YLRE | pmp. PM1645B dosage reag. deox. - in remote |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.4.8 | 22 | 27 | DI |  |  | 0 | 11.1.4 | PM1645B dosage reag. deox. - in remote |  | PM1645B | A23 | PM | 1645 | B | _ | 11 | YLRE | A23PM1645B_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10205 | 205 |  | A23PM1645B_YLH | pmp. PM1645B dosage reag. deox. - in running |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.4.8 | 23 | 27 | DI |  |  | 0 | 11.1.4 | PM1645B dosage reag. deox. - in running |  | PM1645B | A23 | PM | 1645 | B | _ | 11 | YLH | A23PM1645B_YLH | ok | [5 empty] | 0
ID-S01AP1020-10206 | 206 |  | A23PM1645B_YSG | pmp. PM1645B dosage reag. deox. - supply fault |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 | B | 11.1.4.8 | 24 | 27 | DI |  |  | 0 | 11.1.4 | PM1645B dosage reag. deox. - supply fault |  | PM1645B | A23 | PM | 1645 | B | _ | 11 | YSG | A23PM1645B_YSG | ok | [5 empty] | 0
ID-S01AP1020-10207 | 207 |  | A23PM1645B_HSH | pmp. PM1645B dosage reag. deox. - start/stop |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.4.5 | 12 | 15 | DO |  |  | 0 | 11.1.4 | PM1645B dosage reag. deox. - start/stop |  | PM1645B | A23 | PM | 1645 | B | _ | 11 | HSH | A23PM1645B_HSH | ok | [5 empty] | 0
ID-S01AP1020-10208 | 208 |  | A23SR1660_YLRE | stir. SR1660 reag. alkal. - in remote |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.7 | 1 | 2 | DI |  |  | 0 | 11.1.4 | SR1660 reag. alkal. - in remote |  | SR1660 | A23 | SR | 1660 |  | _ | 10 | YLRE | A23SR1660_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10209 | 209 |  | A23SR1660_YLH | stir. SR1660 reag. alkal. - in running |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 |  | 11.1.4.7 | 2 | 2 | DI |  |  | 0 | 11.1.4 | SR1660 reag. alkal. - in running |  | SR1660 | A23 | SR | 1660 |  | _ | 10 | YLH | A23SR1660_YLH | ok | [5 empty] | 0
ID-S01AP1020-10210 | 210 |  | A23SR1660_HSH | stir. SR1660 reag. alkal. - start/stop |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.4.5 | 13 | 15 | DO |  |  | 0 | 11.1.4 | SR1660 reag. alkal. - start/stop |  | SR1660 | A23 | SR | 1660 |  | _ | 10 | HSH | A23SR1660_HSH | ok | [5 empty] | 0
ID-S01AP1020-10211 | 211 |  | A23LI1660 | reag. alkal. - lev. |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | AI | 4/20 mA - 2W | 0 | ∕ | 1000 | mm |  | 11 |  | 11.1.4.2 | 16 | 16 | AI |  |  | 0 | 11.1.4 | alkal. - lev. |  | alkal. | A23 | LI | 1660 |  |  |  |  | A23LI1660 | ok |  |  |  | 0 | 1000 | mm
ID-S01AP1020-10212 | 212 |  | A23PM1665A_YLRE | pmp. PM1665A dosage reag. alkal. - in remote |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.3.1 | 28 | 30 | DI |  |  | 0 | 11.1.3 | PM1665A dosage reag. alkal. - in remote |  | PM1665A | A23 | PM | 1665 | A | _ | 11 | YLRE | A23PM1665A_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10213 | 213 |  | A23PM1665A_YLH | pmp. PM1665A dosage reag. alkal. - in running |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | A | 11.1.3.1 | 29 | 30 | DI |  |  | 0 | 11.1.3 | PM1665A dosage reag. alkal. - in running |  | PM1665A | A23 | PM | 1665 | A | _ | 11 | YLH | A23PM1665A_YLH | ok | [5 empty] | 0
ID-S01AP1020-10214 | 214 |  | A23PM1665A_YSG | pmp. PM1665A dosage reag. alkal. - supply fault |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 | A | 11.1.3.1 | 30 | 30 | DI |  |  | 0 | 11.1.3 | PM1665A dosage reag. alkal. - supply fault |  | PM1665A | A23 | PM | 1665 | A | _ | 11 | YSG | A23PM1665A_YSG | ok | [5 empty] | 0
ID-S01AP1020-10215 | 215 |  | A23PM1665A_HSH | pmp. PM1665A dosage reag. alkal. - start/stop |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.4.5 | 14 | 15 | DO |  |  | 0 | 11.1.4 | PM1665A dosage reag. alkal. - start/stop |  | PM1665A | A23 | PM | 1665 | A | _ | 11 | HSH | A23PM1665A_HSH | ok | [5 empty] | 0
ID-S01AP1020-10216 | 216 |  | A23PM1665B_YLRE | pmp. PM1665B dosage reag. alkal. - in remote |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.4.8 | 25 | 27 | DI |  |  | 0 | 11.1.4 | PM1665B dosage reag. alkal. - in remote |  | PM1665B | A23 | PM | 1665 | B | _ | 11 | YLRE | A23PM1665B_YLRE | ok | [5 empty] | 0
ID-S01AP1020-10217 | 217 |  | A23PM1665B_YLH | pmp. PM1665B dosage reag. alkal. - in running |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | true | = | active | 0 |  | 11 | B | 11.1.4.8 | 26 | 27 | DI |  |  | 0 | 11.1.4 | PM1665B dosage reag. alkal. - in running |  | PM1665B | A23 | PM | 1665 | B | _ | 11 | YLH | A23PM1665B_YLH | ok | [5 empty] | 0
ID-S01AP1020-10218 | 218 |  | A23PM1665B_YSG | pmp. PM1665B dosage reag. alkal. - supply fault |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DI | SPST | false | = | active | 0 |  | 11 | B | 11.1.4.8 | 27 | 27 | DI |  |  | 0 | 11.1.4 | PM1665B dosage reag. alkal. - supply fault |  | PM1665B | A23 | PM | 1665 | B | _ | 11 | YSG | A23PM1665B_YSG | ok | [5 empty] | 0
ID-S01AP1020-10219 | 219 |  | A23PM1665B_HSH | pmp. PM1665B dosage reag. alkal. - start/stop |  |  | ROT.KILN ST.GEN. 1 | A23 DP40 A | A23LP1650 |  | S01AP1020 |  |  |  |  | DO | RELAY | true | → | start | 0 |  | 11 |  | 11.1.4.5 | 15 | 15 | DO |  |  | 0 | 11.1.4 | PM1665B dosage reag. alkal. - start/stop |  | PM1665B | A23 | PM | 1665 | B | _ | 11 | HSH | A23PM1665B_HSH | ok | [5 empty] | 0

## drop11 from check
FROM/TO |  | 11.1.1 | 11.1.2 | 11.1.3 | 11.1.4 | 11.1.5 | 11.1.6 | 11.1.7 | 11.1.8
P23MCC0001 | 130 | 91 | 32 | 0 | 0 | 0 | 0 | 0 | 0
P23JBA1001 | 7 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
P23JBA1002 | 7 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
P23JBD1001 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
P23JBA1003 | 6 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
P23JBD1002 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
P29JB1006 | 13 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0
P29JB1205 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
P29JB1005 | 11 | 0 | 1 | 2 | 8 | 0 | 0 | 0 | 0
P29JB1007 | 6 | 0 | 3 | 3 | 0 | 0 | 0 | 0 | 0
P29JB1002 | 5 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 0
TBD | 17 | 0 | 8 | 6 | 3 | 0 | 0 | 0 | 0
P29JB1010 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0
P23MCC1001 | 88 | 0 | 37 | 48 | 3 | 0 | 0 | 0 | 0
P29JB1004 | 4 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
P29JB1003 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0
P29JB1008 | 13 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 0
P29JB1012 | 6 | 0 | 0 | 2 | 4 | 0 | 0 | 0 | 0
HEPT | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0
P34CAP1701 | 11 | 0 | 0 | 4 | 7 | 0 | 0 | 0 | 0
A23LP1650 | 24 | 0 | 0 | 6 | 18 | 0 | 0 | 0 | 0
|  | 91 | 99 | 91 | 64 | 0 | 0 | 0 | 0

## drop12 from check
FROM/TO |  | 12.1.1 | 12.1.2 | 12.1.3 | 12.1.4 | 12.1.5 | 12.1.6 | 12.1.7 | 12.1.8
CHN1-TDZ2-P32-JBA-1-003 | 5 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0
G12MCC1001 | 272 | 93 | 100 | 72 | 3 | 0 | 0 | 0 | 0
CHN1-TDZ2-A17-JBD-1-003 | 19 | 0 | 0 | 0 | 0 | 2 | 16 | 0 | 0
CHN1-TDZ2-A17-JBD-1-002 | 21 | 0 | 0 | 0 | 0 | 10 | 11 | 0 | 0
S01AP1030 | 66 | 1 | 2 | 3 | 53 | 0 | 0 | 0 | 0 | from location not cler
CHN1-TDZ2-A17-JBD-1-001 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0
A17LP1102 | 4 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0
CHN1-TDZ2-A17-JBA-1-002 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0
CHN1-TDZ2-A17-JBA-1-001 | 4 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0
CHN1-TDZ2-A18-JBA-1-001 | 6 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0
CHN1-TDZ2-A18-JBD-1-002 | 19 | 0 | 0 | 0 | 0 | 0 | 7 | 10 | 2
CHN1-TDZ2-A18-JBD-1-001 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0
A18LP1102 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHN1-TDZ2-A19-JBD-1-002 | 16 | 3 | 0 | 0 | 0 | 0 | 5 | 7 | 1
CHN1-TDZ2-A19-JBD-1-003 | 14 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 8
CHN1-TDZ2-A19-JBD-1-001 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 2
CHN1-TDZ2-A19-JBA-1-002 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0
P30MCC1001 | 38 | 0 | 0 | 0 | 0 | 33 | 5 | 0 | 0
CHN1-TDZ2-P30-JBA-1-001 | 12 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0
CHN1-TDZ2-P30-JBA-1-002 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0
CHN1-TDZ2-P30-JBD-1-001 | 14 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 1
CHN1-TDZ2-P30-JBD-1-002 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 6
CHN1-TDZ2-P30-JBD-1-003 | 4 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0
CHN1-TDZ2-P30-JBA-1-003 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
CHN1-TDZ2-P32-JBD-1-002 | 18 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 12
CHN1-TDZ2-P32-JBD-1-001 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15
CHN1-TDZ2-P32-JBD-1-003 | 12 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 6
CHN1-TDZ2-P32-JBA-1-001 | 4 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
CHN1-TDZ2-P32-JBA-1-002 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0
CHN1-TDZ2-P33-JBA-1-001 | 21 | 0 | 0 | 0 | 0 | 0 | 4 | 7 | 6
P33MCC1001 | 76 | 0 | 0 | 0 | 0 | 41 | 31 | 4 | 0
CHN1-TDZ2-P33-JBA-1-002 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1
CHN1-TDZ2-P33-JBD-1-001 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
CHN1-TDZ2-P33-JBD-1-002 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
P35INV1001 | 15 | 3 | 0 | 3 | 8 | 0 | 0 | 0 | 0
CHN1-TDZ2-P35 LP1101 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
CHN1-TDZ2-P35-JBA-1-001 | 13 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 7
CHN1-TDZ2-P35-JBD-1-001 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
P35MCC1001 | 4 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0
CHN1-TDZ2-P82-JBD-1-002 | 15 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 4
CHN1-TDZ2-P82-JBD-1-001 | 7 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 1
CHN1-TDZ2-P82-JBA-1-001 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
P82LP1152 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0
| 89 | 106 | 104 | 83 | 66 | 112 | 136 | 87 | 90

## module list
11.1.1.1 | DI | 17
11.1.1.2 | DI | 0
11.1.1.3 | DI | 32
11.1.1.4 | DO | 30
11.1.1.5 | SPARE | 0
11.1.1.6 | ELC | 0
11.1.1.7 | AI | 13
11.1.1.8 | AO | 8
11.1.2.8 | DI | 20
11.1.2.7 | DI | 22
11.1.2.6 | DI | 23
11.1.2.5 | DO | 30
11.1.2.4 | SPARE | 0
11.1.2.3 | ELC | 0
11.1.2.2 | AI | 15
11.1.2.1 | AO | 6
11.1.3.1 | DI | 30
11.1.3.2 | DI | 26
11.1.3.3 | DI | 10
11.1.3.4 | DO | 32
11.1.3.5 | SPARE | 0
11.1.3.6 | ELC | 0
11.1.3.7 | AI | 15
11.1.3.8 | AO | 6
11.1.4.8 | DI | 27
11.1.4.7 | DI | 2
11.1.4.6 | DI | 0
11.1.4.5 | DO | 15
11.1.4.4 | AI | 14
11.1.4.3 | ELC | 0
11.1.4.2 | AI | 16
11.1.4.1 | AO | 0
12.1.1.1 | DI | 30
12.1.1.2 | DI | 30
12.1.1.3 | DI | 2
12.1.1.4 | DO | 22
12.1.1.5 | SPARE | 0
12.1.1.6 | ELC | 0
12.1.1.7 | AI | 14
12.1.1.8 | AO | 8
12.1.2.8 | DI | 27
12.1.2.7 | DI | 30
12.1.2.6 | DI | 6
12.1.2.5 | DO | 39
12.1.2.4 | SPARE | 0
12.1.2.3 | ELC | 0
12.1.2.2 | AI | 2
12.1.2.1 | SPARE | 0
12.1.3.1 | DI | 29
12.1.3.2 | DI | 24
12.1.3.3 | DI | 6
12.1.3.4 | DO | 24
12.1.3.5 | SPARE | 0
12.1.3.6 | SPARE | 0
12.1.3.7 | AI | 0
12.1.3.8 | SPARE | 0
12.1.4.8 | DI | 26
12.1.4.7 | DI | 3
12.1.4.6 | DI | 6
12.1.4.5 | DO | 31
12.1.4.4 | SPARE | 0
12.1.4.3 | SPARE | 0
12.1.4.2 | AI | 0
12.1.4.1 | SPARE | 0
12.1.5.1 | DI | 28
12.1.5.2 | DI | 27
12.1.5.3 | DI | 0
12.1.5.4 | DO | 31
12.1.5.5 | SPARE | 0
12.1.5.6 | AI | 11
12.1.5.7 | AI | 9
12.1.5.8 | AO | 6
12.1.6.8 | DI | 25
12.1.6.7 | DI | 27
12.1.6.6 | DI | 24
12.1.6.5 | DO | 30
12.1.6.4 | SPARE | 0
12.1.6.3 | AI | 15
12.1.6.2 | AI | 8
12.1.6.1 | AO | 7
12.1.7.1 | DI | 18
12.1.7.2 | DI | 19
12.1.7.3 | DI | 0
12.1.7.4 | DO | 32
12.1.7.5 | SPARE | 0
12.1.7.6 | AI | 14
12.1.7.7 | AI | 0
12.1.7.8 | AO | 4
12.1.8.8 | DI | 27
12.1.8.7 | DI | 28
12.1.8.6 | DI | 17
12.1.8.5 | DO | 2
12.1.8.4 | SPARE | 0
12.1.8.3 | AI | 16
12.1.8.2 | AI | 0
12.1.8.1 | SPARE | 0
11.1.5.1 | DI | 0
11.1.5.2 | DI | 0
11.1.5.3 | DI | 0
11.1.5.4 | DO | 0
11.1.5.5 | SPARE | 0
11.1.5.6 | SPARE | 0
11.1.5.7 | AI | 0
11.1.5.8 | AO | 0
11.1.6.8 | AI | 0
11.1.6.7 | SPARE | 0
11.1.6.6 | SPARE | 0
11.1.6.5 | SPARE | 0
11.1.6.4 | SPARE | 0
11.1.6.3 | SPARE | 0
11.1.6.2 | SPARE | 0
11.1.6.1 | SPARE | 0